# Asbestos Management Plan

| Version number | 2.0 |
| --- | --- |
| Consultation Groups | Asbestos Safety Group |
| Approved by (Sponsor Group) | Health, Safety and Security Committee |
| Date approved | 30th March 2024 |
| Ratified by | Service Delivery Board |
| Date ratified | 27th November 2024 |
| Name of originator/author | Interim Senior Engineering Manager Frankham Consultancy Group Assistant Director of Estates – Engineering and Infrastructure |
| Executive Director lead | Director of Estates, Facilities & Capital Development |
| Implementation Date | November 2024 |
| Last Review Date | November 2024 |
| Next Review Date | November 2027 |

| Services | Applicable to |
| --- | --- |
| Trust wide | Yes |
| Mental Health and LD | Yes |
| Community Health Services | Yes |
| Primary care | Yes |

Version Control Summary

| Ver | Date | Author | Status | Comment |
| --- | --- | --- | --- | --- |
| 0.1 | 29th November 2022 | Hadi Shukir (Interim Senior Engineering Manager) | Draft | Initial Plan |
| 0.1 | 24th February 2023 | Adam Hunt (Frankham Consultancy Group) | Draft | Plan reviewed by Asbestos Subject Matter Expert |
| 0.2 | 14th March 2023 | Hadi Shukir (Interim Senior Engineering Manager) | Draft | Draft Plan updated following review by Director of Estates |
| 1.0 | 27th July 2023 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Final | Ratified by the Assistant Director of Estates, Engineering, and Infrastructure |
| 1.1 | 15th January 2024 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Update | Plan updated following appointment of Asbestos Independent Advisor |
| 1.2 | 11th February 2024 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Update | Flow charts and legislation sections updated. |
| 1.3 | 8th November 2024 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Review | Policy format updated as per requirements of the Trust’s ‘Policy and Procedure for the Development, Review and Control of Trust Approved Procedural Documents.’ Submitted to Service Delivery Board. Asbestos Register section of this document updated. |
| 2.0 | 27th November 2024 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Final | Policy ratified at the Trust’s Service Delivery Board. |

Contents

Paragraph										         		         Page

1	Asbestos Management Plan Gateway	7

2	Executive Summary	8

3	Objectives	8

4	Scope	9

5	Statutory Requirement	9

6	Exclusions	9

7	Derogations	9

8	Definitions	10

9	Related Trust Policies & Procedures	12

10	Roles and Responsibilities	12

11	Asbestos Register	12

12	Location of Asbestos	14

13	Asbestos Surveys	14

14	Asbestos Management Strategy	15

15	Contractors	16

16	Asbestos Remediation / Removal	16

17	Asbestos Incident Reporting RIDDOR (Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013)	18

18	Asbestos Safety Group	18

19	Asbestos Procedures and Processes	18

20	References	25

21	Asbestos Management Plan Review	25

22	Asbestos Register	26

23	Appendix A: Policy Equalities Impact Assessment	85

24	Appendix B: Policy Submission Form / Checklist	87

# Asbestos Management Plan Gateway

Please complete the checklist and tables below to provide assurance around the Asbestos Management Plan review process.

Asbestos Management Plan Checklist

☒ I have involved everyone who should be consulted about this policy/guidance ☒ I have identified the target audience for this policy/guidance ☒ I have completed the correct template fully and properly ☒ I have identified the correct approval route for this policy/guidance ☒ I have saved a word version of this policy/guidance for future reviews and reference

Please set out what makes you an appropriate person to conduct this review:

I am the Assistant Director of Estates, Engineering, and Infrastructure

Please set out the legislation, guidance, and best practice you consulted for this review:

The Health and Safety at Work etc. Act 1974 Control of Asbestos at Work Regulations (CAR) 2012 Management of Health and Safety at Work Regulations 1999 Construction (Design and Management) Regulations 2015 (CDM 2015) Other references as detailed within this Asbestos Management Plan

Please identify the key people you involved in reviewing this policy why, and when:

The Asbestos Safety Group on 27th March 2024. The Health, Safety and Security Committee on 20th March 2024. The Service Delivery Board 27th November 2024.

Summarise the key changes you have made and why:

This is a working document and as such will be updated on a regular basis. All changes are to be captured within the Version Control Summary section of this document.

# Executive Summary

The East London NHS Foundation Trust’s (ELFT) Asbestos Management Plan (AMP) is aimed at the management and monitoring of all Asbestos Containing Materials (ACM) at all ELFT sites directly under its control and must be used in conjunction with the ELFT Asbestos Safety Policy and other pertinent policy / management documents.

The Asbestos Management Plan (AMP) is a risk-management approach to the management, monitoring, and control of Asbestos Containing Materials (ACM) that establishes good practices. This plan is designed to.

- Identify potential Asbestos related hazards, considers practical aspects and details appropriate control measures.

- Provide the guidance, instruction, specification, and infrastructure for the implementation of ELFT’s Asbestos Management and Monitoring programme to comply with legislation and guidance as required and appropriate. This includes the control of Asbestos to provide a practical framework for maintaining the safety of our colleagues and ensuring compliance with all relevant guidance within properties under the control of ELFT.

As part of ELFT commitment to compliance with Health and Safety Executive Guidance and the Approved Code of Practice it is necessary that all design, installation, commissioning, regular tests, and checks set out in this document shall be carried out even if they cause disruption to services, and that comprehensive records will be maintained.

It is acknowledged that it is for ELFT management and staff to do all that is reasonably practicable to achieve compliance with the guidance requirements detailed within this Asbestos Management Plan (AMP) and all other regulations and guidance regarding Asbestos under ELFT’s control. It is therefore considered essential that management and staff should work together to achieve an environment compatible with the provision of the highest quality services where health hazards to patients, staff and others are minimised, so far as is reasonably practical.

It is also expected that this Asbestos Management Plan (AMP) will be complied with by all the ELFT employees and by all appointed contractors, in whatsoever capacity, with or without contractual agreements.

The Asbestos Management Plan (AMP) is a living document which is kept under continual review and is a standing agenda item at the Asbestos Safety Group meetings. It is available on the ELFT Intranet, by request from the Assistant Director or Estates, Engineering, and Infrastructure, and will be shared with the Asbestos Safety Group attendees prior to every meeting.

# Objectives

Asbestos has been used in hundreds of different products over the last 150 years and was commonly used in many different types of building materials; particularly from the 1950’s to the mid 1980’s. Asbestos cement was still in use up until 1999 in a variety of premises and materials. As a result of its overwhelming health damaging effects, it is illegal to use asbestos in the construction or refurbishment of any premises. However, many thousands of tonnes of it were used and much of this is still in place. Trust buildings do contain Asbestos and Asbestos Containing Materials (ACM). Breathing in air containing Asbestos fibres can lead to asbestos-related diseases; mainly cancers of the lungs (mesothelioma) and chest lining. There is usually a long delay between first exposure to Asbestos and the onset of asbestos related disease, this can vary from 15 to 60 years and once diagnosed the prognosis is poor. Only by preventing or minimising these exposures will Asbestos-related disease eventually be reduced.

The objective of this Asbestos Management Plan (AMP) is therefore to ensure effective management, monitoring, and control of Asbestos Containing Materials throughout ELFTs premises to minimise the risk of exposure to Asbestos.

# Scope

This Asbestos Management Plan (AMP) applies to all demises that are directly under the control of ELFT and have been identified as containing Asbestos Containing Materials (ACM).

# Statutory Requirement

ELFT has a statutory duty to.

- Take action to manage the risks from asbestos.

- Prevent employees or anyone else who may be affected from being exposed to asbestos, or where this is not practicable, to reduce exposure to the lowest reasonably practicable level.

- Make a suitable and sufficient assessment of risk prior to work being carried out with asbestos and then take steps to control and monitor exposure.

- Provide information, instruction or training for its employees that may meet asbestos during their work.

- Maintain workplace premises to protect occupants and workers at those premises.

- Make an assessment to the Health and Safety risks of its employees and people not employed by ELFT (such as visitors, service users, residents, or contractors) arising out of or in connection of with the conduct of their business – and to make appropriate arrangements for protecting those people’s health and safety.

- Maintain workplace premises to protect occupants and workers at those premises.

- Pass on information about the state and condition of any premises before any work commences and to ensure that the health and safety file for the project is retained and to provide access to all involved in the project.

- Provide suitable and sufficient information on asbestos risk from their Asbestos Register. In agreement with the Principal Designer / Principal Contractor, ELFT may request that an asbestos survey is procured on ELFTs behalf at the pre-construction stage. However, the legal duty to ensure that the information is provided remains with ELFT and so the Estates / Digital Project Manager must ensure that where necessary, the survey is completed and disseminated. ASB5 notifications and LARC plans of work (for both licensable and non-licensable work) should be provided to the appointed ELFT Asbestos Consultant as soon as they are available. At the end of the notifiable period the PC and PD must supply the Principal Designer / Contractor must supply the ELFT Asbestos Consultant with updated asbestos register for the area, detailing what asbestos has been removed or remediated and what asbestos remains. The ELFT Asbestos register must then be updated.

# Exclusions

This Asbestos Management Plan (AMP) shall not apply for the area and period defined within the F10 notification. A separate AMP must be documented by the Principal Contractor (PC) for the area under such circumstances for the duration of the notification period.

# Derogations

Where any of the requirements of this AMP or any other relevant legislation or guidance, whether in-whole or in-part thereof cannot be adhered to as detailed, formal application for derogation must be submitted to the Trust’s Asbestos Independent Advisor and the Asbestos Safety Group for approval. Requests for derogation must be accompanied by a robust rationale detailing the reasons for seeking derogation and alternative processes and procedures proposed. No deviation from the requirements of this Asbestos Management Plan (AMP), either implicit or explicit, is allowed without suitably signed and dated approval.

# Definitions

| Term | Definition |
| --- | --- |
| ACM / ACMs | Asbestos Containing Material / Asbestos Containing Materials |
| AIA | Asbestos Independent Advisor |
| AIB | Asbestos Insulating Board – Any flat sheet, tile or building board consisting of a mixture of asbestos and other material except. - Asbestos cement or. - Any article of bitumen, plastic, resin, or rubber which contains asbestos, and the thermal or acoustic properties of the article are incidental to its main purpose. |
| AMP | Asbestos Management Plan |
| ASG | Asbestos Safety Group |
| ASP | Asbestos Safety Policy |
| Asbestos | Asbestos means the following fibrous silicates. - Asbestos Actinolite - Asbestos Grunerite (Amosite) (Brown Asbestos) - Asbestos Anthophyllite - Chrysotile (White Asbestos) - Crocidolite (Blue Asbestos) - Asbestos tremolite These groups of Asbestos fibres differ in their mechanical and chemical properties. The different types of Asbestos can be found on their own or as a mixture with any of the other fibres. All Asbestos fibres are classed as dangerous carcinogens, but blue and brown Asbestos are thought to be more dangerous than white asbestos. One cannot identify them just by their colour. |
| Asbestos Cement | A material which is predominantly a mixture of cement and chrysotile and which when in a dry state absorbs less than 30% water by weight. |
| Asbestos Coating | A surface coating which contains asbestos for fire protection, heat insulation or sound insulation but does not include textured decorative coatings. |
| Asbestos Insulation | Any material containing asbestos which is used for thermal, acoustic, or other insulation purposes (including fire protection) except. - Asbestos cement, asbestos coating, or asbestos insulating board or. - Any article of bitumen, plastic, resin, or rubber which contains asbestos, and the thermal or acoustic properties of the article are incidental to its main purpose. |
| Asbestos Register | A formal record of present or presumed Asbestos within ELFT properties. It contains details of the locations of ACMs, their extent and condition and their form (product type tiles, board, cement sheets etc) and what the ACM looks like. This formal register is regularly updated. |
| Contractor / Supplier | A contractor / supplier or partner organisation who provides services to ELFT. |
| COSHH | Control of Substances Hazardous to Health regulations 2002 |
| DIPC | Director of Infection Prevention and Control |
| Duty Holder | Duty Holder is defined within Regulation 4, Control of Asbestos Regulations 2012. It is primarily the responsibility of the designated Duty Holder, or Duty Holders, where the responsibility is shared, to ensure that asbestos is effectively controlled and managed within their premises. |
| HSAWA | Health and Safety at Work etc. Act 1974 |
| IPC | Infection Prevention and Control |
| Licensable work with Asbestos | Is work. - Where the exposure to asbestos to employees is not sporadic and or low intensity or. - In relation to which the risk assessment cannot clearly demonstrate that the control limit will not be exceeded or. - On Asbestos Coating or. - On Asbestos Insulating Board or Asbestos Insulation for which the risk assessment. - Demonstrates that the work is not sporadic or low intensity or. - Cannot clearly demonstrate that the control limit will not be exceeded or. - Demonstrates that the work is not short duration work |
| PC | Principal Contractor |
| PHE | Public Health England |
| PPE | Personal Protective Equipment – All equipment (including clothing) which is intended to be worn or held by a person at work and which protects that person against one or more risks to that person’s health, and any addition or accessory designed to meet that objective. |
| PPM | Planned Preventative Maintenance |
| SOM | Senior Operational Manager |
| Supplier / Contractor | An ELFT appointed company or partner who is responsible for undertaking maintenance activities (including PPM, reactive and remedial works) or project works on behalf of ELFT. |
| Textured decorative coatings | Decorative and textured finishes, such as paints and ceiling and wall plasters which are used to produce visual effects, and which contain Asbestos. These coatings are designed to be decorative, and any thermal or acoustic properties are incidental their purpose. |
| UKAS | United Kingdom Accreditation Service |

# Related Trust Policies & Procedures

The following Trust polices should be read in conjunction with this policy.

- Health and Safety Policy

- Infection Prevention and Control Policy Manual

- Asbestos Safety Policy

- Estates Operational Policy (due for release in 2024)

# Roles and Responsibilities

The Trust’s roles and responsibilities are detailed within the Trust’s Asbestos Safety Policy.

# Asbestos Register

The Asbestos Register has been included within this Asbestos Management Plan.

The Asbestos Register is held in electronic format and is managed and maintained by the Estates department.

ELFT properties that currently have identified ACMs are.

- 115 Balaam Street

- 117 Balaam Street

- 119 Balaam Street

- 121 Balaam Street

- 15 Homerton Row

- 19-21 High Street South

- 29 Romford Road

- 385 Barking Road

- 409 Stratford High Street

- 67 High Street South

- Alie Street

- Appleby HC

- Barford Avenue

- Beacon House

- Beech Close Resource Centre

- Calnwood Court

- Cedar House

- Charter House

- Crombie House

- Donald Winnicott

- EMPOWA Wellbeing

- Five Elms HC

- Ilford Chambers

- JHC - Elizabeth Fry Building

- JHC - John Warburton Building

- JHC - Whitbread Building

- Johnson Street

- Joyce Campbell

- Leighton Road Surgery

- Mountbatton House

- Rush Court - 5,7,9

- The Crescent

- The Lawns

- The Lodge

- Twinwoods Admin Block

- Twinwoods CRC

- Twinwoods Raymond Smith

- Twinwoods Russell Block

- Twinwoods Whitchurch Centre

- Twinwoods Whitbread Centre

- Upminster Medical Centre

- Whichellos Wharf and Whichellos Wharf Cottage

- Wolfson House

- York House

The Estates department shall always be contacted prior to works where Asbestos may be disturbed.

# Location of Asbestos

As long as Asbestos is in good condition and is not being (or is not likely to be) disturbed or damaged, there is negligible risk. However, if it is disturbed or damaged, it can become a danger to health, because asbestos fibres are then released into the air and people may breathe them in.

Asbestos is often contained in materials such as:

- Loose packing for fire breaks in ceiling voids and risers.

- Moulded or preformed lagging - generally used in thermal insulation of pipes and boilers.

- Sprayed Asbestos - generally used  as fire protection  in ducts, fire breaks, panels, partitions, and on asbestos cement sheets around structural.

- Steel work

- Insulating boards used for fire protection, thermal insulation, partitioning and ducts, as soffits and ceiling tiles or wall panels

- Millboard, paper, and paper products used for insulation of electrical equipment (Asbestos paper has also been used as a fire-proof facing on

- Wood fibreboard)

- Asbestos cement products, which can be fully or  semi-compressed into flat or corrugated sheets (corrugated sheets are largely used as roofing and

- Wall cladding

- Other Asbestos cement products include gutters, rainwater & groundwater pipes, and water tanks.

- Certain textured or sprayed on coatings (including Artex).

- Bitumen roofing material, vinyl or thermoplastic floor tiles, window sash cords, brake pads, and gaskets

# Asbestos Surveys

The Assistant Director of Estates, Engineering, and Infrastructure, via the Trust’s Compliance & Business Services Manager, is responsible for ensuring that ELFT has a proactive survey programme in place to ensure all managed properties have a current asbestos management survey in place. Whenever intrusive works are planned to a building, a more in-depth refurbishment and demolition survey is carried out which is specific to the planned scope of works.

Furthermore, periodic Asbestos Reinspection Surveys are carried out on an annual basis to record present status of asbestos containing materials (ACMs), and to attempt access into previously non-accessed areas. Where a survey has not been carried out ACMs are presumed to be present unless known otherwise.

A complete Asbestos Register for all the trust’s sites has been compiled within this management plan based on the survey information available. Completed survey reports are held both centrally by the ELFT Estates Compliance Management team.

All identified and presumed ACMs have been given a risk assessment score. These scores are formed from a Material Assessment algorithm and a Priority Assessment algorithm. These algorithms consider the condition of the asbestos (Material) and the likelihood of people being exposed to fibres (Priority). Material and Priority assessment scores are then combined to form a total outline risk score. This score indicates priorities for action. These priorities can then be used to develop the action plan.

All surveys shall be undertaken by UKAS accredited, ELFT authorised suppliers specialising in this activity. The supplier shall be able to demonstrate a previous history of working to the requirements of the HSE guidance HSE 264: The Survey Guide, have suitable liability insurance and the appropriate license as required by the Control of Asbestos regulations (CAR 2012).

Survey types as defined in HSG: 264 are as follows:

## Asbestos Management Survey

A management survey is the standard survey. Its purpose is to locate, as far as reasonably practicable, the presence and extent of any suspect ACMs in the building which could be damaged or disturbed during normal occupancy, including foreseeable maintenance and installation, and to assess their condition. Management surveys will often involve minor intrusive work and some disturbance. The extent of intrusion will vary between premises and depend on what is reasonably practicable for individual properties (e.g., the type of building, the nature of construction, accessibility etc).

A management survey includes an assessment of the condition of the various ACMs (Material Assessment) and their ability to release fibres into the air if they are disturbed. The material assessment will give a good initial guide to the priority for managing ACMs as it will identify the materials which will most readily release airborne fibres if they are disturbed. The survey involves sampling and analysis to confirm the presence or absence of ACMs. A management survey can also involve presuming the presence or absence of asbestos.

## Refurbishment and demolition surveys

A refurbishment and demolition survey are needed before any refurbishment or demolition work is carried out. This type of survey is used to locate and describe, as far as reasonably practicable, all ACMs in the area where the refurbishment work will take place or in the whole building if demolition is planned. The survey will be fully intrusive and involve destructive inspection, as necessary, to gain access to all areas, including those that may be difficult to reach. A refurbishment and demolition survey may also be required in other circumstances, e.g., when more intrusive maintenance and repair work will be carried out or for plant removal or dismantling.

A refurbishment survey includes an assessment of the condition of the various ACMs (Material Assessment) and their ability to release fibres into the air if they are disturbed. The material assessment will give a good initial guide to the priority for managing ACMs as it will identify the materials which will most readily release airborne fibres if they	are disturbed. The survey involves sampling and analysis to confirm the presence or absence of ACMs.

The relevant Project Manager (Including Digital Project Managers) must arrange for a survey to be conducted by the Approved Consultant. Intrusive work includes all demolition or breaking out, forming openings (of any size) in walls, floors, and ceilings, opening ducts, boxing, or voids, lifting of coverings etc.  The cost of this survey must be met from the project budget.

# Asbestos Management Strategy

ELFT’s Management Strategy is to assess the risks from ACMs and implement procedures to manage them by:

- Maintain an up-to-date formal Asbestos Register

- Ongoing monitoring, auditing, and reviewing of asbestos information.

- Sharing asbestos information

- Training relevant employees

- Ensuring contractors skills matrices include asbestos awareness and relevant qualifications.

- Managing and monitoring the risk of all known or suspected ACMs

- Removing high risk ACMs and encapsulating or managing / leaving in situ where appropriate

The overall aim is to ensure that all ACMs in premises are effectively managed in line with HSG 227 and the risks reduced to the lowest practical level. ELFT achieve this through initial surveys, re-inspections, and monitoring and remedial or removal works where appropriate. ELFT will continuously assess these programmes and where the cost benefit is found to favour removal of ACM’s this will be completed to eliminate the need to monitor and manage.

Generally, as there is no risk from ACMs if people are not exposed to the released fibres, ELFT manage ACMs in situ where possible. However, where the findings from the priority and material risk assessment algorithms recommends removal, ELFT will follow those recommendations. This means that removal is considered on a case-by-case basis and prioritised in accordance with the risk assessment score. Measures that are needed in all cases where ACMs are present will be to:

- Communicate its presence with employees, contractors, and others.

- Monitor the condition of the ACM.

- Putting a safe system of work in place.

# Contractors

Maintenance contractors are responsible for checking the Asbestos Register and carrying out risk assessments before undertaking any work in ELFT properties. They must notify ELFT Estates and the Asbestos Independent Advisor, and cease work, if damaged or disturbed known or suspected ACMs is encountered.

ACM's may be contained and concealed within some plant and equipment, where it may not have been possible to fully identity these as part of a management survey (due to being live / in use at the time) - it must therefore be presumed that asbestos is present until its absence can be confirmed when the item is no longer live or in use.  Contractors must ensure that any equipment that is to be disposed of that potentially contains ACM must be done in the correct manager and with notification to the estates and the Asbestos Management Consultant.

# Asbestos Remediation / Removal

Where identified through on-going periodic re-inspections, or targeted asbestos refurbishment / demolition surveys that an asbestos material requires remedial work, the nominated asbestos contractor will propose a recommendation. Recommendations for remedial works are likely to be.

## Protecting / Enclosing

Protecting known ACMs will mean building or placing of a physical barrier of some sort to prevent any accidental contact with or disturbance of the material. This could be in the form of bollards, railings or suitable over boarding.

Enclosing the ACM involves making an airtight barrier around it which will stop the spread of any airborne asbestos fibres. The edges and corners of the barrier must be completely sealed. Enclosing the ACM is a good option if it is in reasonable condition, but it won’t protect it from being damaged. If it is necessary to access this area for maintenance or it’s possible the building fabric around it may fail, ELFT will look to remove ACMs where practicable. Any enclosures erected in around areas of fire compartmentation should not compromise this and will need to be made to complement the existing fire resistance.

Any enclosed ACM’s must be shown in the register for that site and the enclosure labelled to clearly show that asbestos is present behind it. The enclosure will form part of our ongoing monitoring strategy.

If the ACMs to be enclosed are a licensable material and the enclosure building is liable to disturb the ACM, this work will need to be done by our framework licensed asbestos removal contractor.

## Encapsulation

There are two types of encapsulants: bridging and penetrating.

### Bridging

Bridging types will form a surface covering to the material whilst penetrating types will sink into the material and then set to form a solid bond throughout it. Bridging encapsulants include high build elastomers, cementitious coatings, and polyvinyl acetate (PVA). The different types of encapsulants available will suit different circumstances and ACMs. High build elastomers can provide substantial impact resistance as well as elasticity, especially when they incorporate a reinforcing membrane. These types of encapsulants are reported to provide up to 20 years of life if undisturbed. Cementitious coatings are generally spray-applied and are compatible with most asbestos applications. They provide a hard-set finish but may crack over time. PVA is used for sealing of asbestos insulating board and may be spray or brush applied. It is not suitable for use on friable ACMs such as insulation or sprayed coatings. PVA will only provide a very thin coating and may not be suitable as a long-term encapsulant.

### Penetrating

Penetrative encapsulants are spray-applied and will penetrate friable asbestos materials, strengthening them as well as providing an outer seal. The fire-resistant properties of the encapsulant will be an important consideration if the function of the ACM was to provide fire resistance. Encapsulation works are carried out by licensed asbestos removal contractors.

## Repair

This an option to be considered carefully. To be considered for repair any damage must be slight, as such any repair should be restricted to patching / sealing small areas and making good slight damage to any enclosures we may have that are protecting ACMs. If the ACM is to be repaired, there are several methods that can be employed depending upon the type of material. Damaged asbestos sheets or tiles can be sprayed with PVA sealant or a similar type of sealant such as ET150. PVA will only provide a very thin coating and shouldn’t be seen as a long-term solution, particularly where there is significant damage. ET150 will be the preferred product for this task. Unsealed and undamaged ACM’s may be treated with a sealant to prevent deterioration of the exposed surface. Asbestos cement should be sealed using an alkali-resistant and water-permeable sealant. If only one side of an ACM is treated with an impermeable product it can lead to premature failure of the ACM. Fire protection made by any ACMs needs to be maintained so any products used in these areas must also have fire-retardant properties. ELFT will generally appoint any ACM repair work to a licensed asbestos removal contractor.

## Remove

Where ACMs have been identified during survey and are in a poor condition or are deemed to be in a vulnerable position and could be damaged, exploring the other management options above should be done. If it’s not practical to repair, enclose or encapsulate these ACMs, removal will be the preferred option. ACMs will also need to be removed if they are in an area that’s going to be part of refurbishment works which will disturb the ACM, or if the building is due to be demolished. ELFT will look to have this carried out by a licensed asbestos removal contractor.

Removal of asbestos or remedial works to asbestos, such as encapsulation, is hazardous and must be carried out under strictly controlled conditions. All works are currently carried out by suitably qualified and competent contractors. For non-licensed, low risk responsive repairs only, works are carried out in accordance with a risk assessment by the in-house repairs team, and the supervisors need to ensure that sufficient safety and training measures are in place. The relevant contract manager ensures they have appropriately controlled the risk through POW RA and relevant training records. No asbestos remedial work will be undertaken by in house staff.

# Asbestos Incident Reporting RIDDOR (Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013)

As per the Trust’s Health and Safety Policy the Trust’s Governance and Risk Department has specific responsibility for notifying accidents and dangerous occurrences to the Health and Safety Executive under the Reporting of Injuries, Diseases and Dangerous Occurrences Regulations.

The Health and Safety Executive guidance ‘When does inadvertent exposure to asbestos constitute a reportable incident under RIDDOR?’ states.

The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013 (RIDDOR) places duties on employers, the self-employed and people in control of work premises (the responsible person) to report certain serious workplace accidents, occupational diseases and specified dangerous occurrences (near misses).

Exposure to asbestos is reportable under RIDDOR when a work activity causes the accidental release or escape of asbestos fibres into the air in a quantity sufficient to cause damage to the health of any person.

Such situations are likely to arise when work is carried out without suitable controls, or where those controls fail – they often involve:

- use of power tools (to drill, cut etc) on most ACMs.

- work that leads to physical disturbance (knocking, breaking, smashing) of an ACM that should only be handled by a licensed contractor e.g. sprayed coating, lagging, asbestos insulating board (AIB)

- manually cutting or drilling AIB

- work involving aggressive physical disturbance of asbestos cement e.g. breaking or smashing.

If these activities are carried out without suitable controls, or the precautions fail to control exposure, these would be classed as a 'dangerous occurrence' under RIDDOR and should be reported.

Remember, if you need to report a dangerous occurrence relating to asbestos, you should review your asbestos management plan or your working practices.

# Asbestos Safety Group

The ASG Terms of Reference are held by the ELFT Estates Management team. They are provided to ASG attendees and are reviewed on an annual basis.

# Asbestos Procedures and Processes

## Asbestos Emergency Procedures

If damaged or unexpected materials are encountered which are suspected ACM, or consultants identify ACMs that have a significant risk (for example ACMs that have a high likelihood of being disturbed) then colleagues, contractors and consultants are required to stop work immediately and undertake the emergency procedure detailed below.

The incident shall also be raised on the Trust’s Incident Management System (InPhase). The Health, Safety, Security & Emergency Planning Manager and Estates department shall also be contacted immediately.

### Asbestos Emergency Procedure Flowchart

## Asbestos Management Processes (Aligned to HSG 227 Appendix Flowcharts)

Materials suspected of Containing Asbestos

Sprayed Asbestos Coatings, Pipe and Vessel Insulation Flow Diagram

## Asbestos Insulating Boards and Insulating Blocks Flow Diagram

## Other Asbestos Materials

The Other Asbestos Materials Flow Diagram covers products not included within the previous two flow diagrams (the Sprayed Asbestos Coatings, Pipe and Vessel Insulating Blocks flow diagram and the Asbestos Insulating Boards and Insulating Blocks Flow Diagram), such as asbestos cement, textiles, gaskets, ropes, and encapsulated products such as vinyl and thermoplastic tiles, roofing felts etc. Materials which are encapsulated in a resilient matrix will have limited ability to release fibres, therefore Asbestos in reinforced plastics, vinyl, resins, rubber, mastics, bitumen, paints, flexible plasters, and cements have little opportunity to release fibres unless the matrix is removed (e.g., degraded, dissolved, or burnt) or subject to high levels of abrasion (e.g., the use of power tools). Management of these types of materials so maintenance workers do not use abrasive methods and power tools is usually sufficient to minimise airborne asbestos releases. Sealing may be considered if remedial action is deemed to be necessary. However, unless the damage is significant or they are in a vulnerable position, urgent remedial action is unlikely to be necessary and you should simply remove these products following the correct precautions (see HSG227 paragraph 19 – 23 for further information) when they come to the end of their useful life, or before refurbishment or demolition.

Products which are less well encapsulated (e.g., asbestos textiles and gaskets), will release fibres more readily and use of controlled work methods by maintenance workers and enclosure or sealing to prevent damage may be necessary in some circumstances.

### Other Asbestos Materials Flow Diagram

# References

- Health and Safety at Work etc. Act 1974

- The Management of Health and Safety at Work Regulations 1999

- Control of Asbestos at Work Regulations (CAR) 2012

- Health and Safety Executive - Approved Code of Practice and Guidance – Control of Asbestos Regulations 2012 – Managing and Working with Asbestos

- Building Act 1984

- Building Safety Act 2022

- Fire Safety Act 2021

- Construction (Design and Management) Regulations 2015

- The Control of Substances Hazardous to Health Regulations 2002

- Public Health (Infectious Diseases) Regulations 1988

- The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013 (RIDDOR)

- The Workplace (Health, Safety and Welfare) Regulations 1992

- Confined Spaces Regulations 1997

- Personal Protective Equipment at Work Regulations 2002

- The Health and Social Care Act 2008 (Regulated Activities) Regulations 2014

- Health and Safety Executive Guidance

  - HSG 264 – Asbestos – The Survey Guide

  - HSG 227 – A Comprehensive Guide to Managing Asbestos in Premises

  - HSG 247 – Asbestos – The licensed contractors’ guide

  - HSG 248 – Asbestos – The Analysts’ Guide

- Health and Safety – Equipment and Method EM Series -  https://www.hse.gov.uk/pubns/guidance/emseries.htm

The Trust recognises its duties and legal responsibilities under these Act and Regulations and has compiled this Asbestos Management Plan (AMP) that sets out the planned approach for the Trust to achieve compliance with all relevant Health and Safety Legislation and Approved Codes of Practice (ACOP) within the Trust’s owned or maintained properties.

# Asbestos Management Plan Review

The AMP will be reviewed.

- At each Asbestos Safety Group meeting.

- As and when there are changes to any legislation and national policy governing this area of work.

- Periodically to ensure the on-going suitability, adequacy and effectiveness of the Asbestos Management Plan and Procedures is undertaken at least annually.

- Annually or when there is a change in legislation or ELFT has recognised improved systems of work.

- More frequent reviews will be undertaken whenever warranted e.g., whenever there is a significant change to the structure of the organisation, or personnel responsible for its implementation.

Relevant colleagues including Senior Managers are notified where revisions have been undertaken and that the revised procedure is sent by all Senior Managers to their staff.

# Asbestos Register

| Code | Area | Borough | Property Name | Property Area | Property Address | Floor Level | Area / Ward | Room No / Name | Notes | Asbestos Type | Comments | Recommended Action | Risk Category |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | Room 04 - Corridor | Ground floor - corridor (Rm 04) - no access below laminate flooring | No access | Laminate flooring, plastered walls, plasterboard ceiling | Further investigation required prior to works | N/A |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | Room 10 - Entrance Lobby | Ground floor - entrance lobby (Rm 10) - no access below laminate flooring | No access | Laminate flooring, plastered walls, plasterboard ceiling | Further investigation required prior to works | N/A |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | Room 12 - Group Room | Ground floor - group room (Rm 12) - no access below laminate flooring | No access | Laminate flooring, plastered walls, plasterboard ceiling | Further investigation required prior to works | N/A |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | First Floor |  | Room 19 - Unknown | First floor - unknown room (Rm 19) - inaccessible | No access | Door code unknown. Former shower room | Further investigation required prior to works | N/A |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E002 - Roof Area | External - roof areas (E002) - roof tiles | Chrysotile | Imitation slate tiles to roof, metal and plastic rainwater gods, wood soffits and facias. Presumed due to height | Manage | D |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof space - loft space (LS01) - ceiling felt | Chrysotile | Felt to ceiling, timber beams, mmmf insulation, calorifier. Presumed due to access issues | Manage | D |
| 2143 | London | Newham | 115 Balaam Street | 115 Balaam Street | 115 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof Void - Loft Space (LS01) -All areas - Limited Access | No Access | Felt to ceiling, timber beams, mmmf insulation, calorifier. Limited access due to the lack of floorboards | Further investigation required | N/A |
| 2129 | London | City & Hackney | 15 Homerton Row | 15 Homerton Row | 15 Homerton Row Rehabilitation Centre, London, E9 6ED | External |  | E01 | External (E01) - undercloaking - cement | Crocidolite (or unknown) | Slate tiles to roof, plastic guttering, UPVC fascia, soffits and windows, brick walls, concrete floor | Manage | C |
| 2129 | London | City & Hackney | 15 Homerton Row | 15 Homerton Row | 15 Homerton Row Rehabilitation Centre, London, E9 6ED | Ground Floor |  | 30 - Boiler Room | Ground floor - boiler room (30) - behind Thames Gas sign - cement | Chrysotile | Concrete ceiling, solid and plasterboard walls, concrete floor metal pipework, 2 x boilers, calorifier | Manage | D |
| 2129 | London | City & Hackney | 15 Homerton Row | 15 Homerton Row | 15 Homerton Row Rehabilitation Centre, London, E9 6ED | Ground Floor |  | 30 - Boiler Room | Boiler room (30) - Wall mounted electrics - Textile internals | Chrysotile | Concrete ceiling, solid and plasterboard walls, concrete floor metal pipework, 2x boilers, calorifier. | Manage | D |
| 2150 | London | Newham | 19/21 High Street South | 19/21 High Street South | 19/21 High Street South, East Ham, London E6 6EN (Sickle Cell Centre) | External |  | E01 | External - external (E01) - undercloaking - cement | Crocidolite | Slate tiles to roof, plastic guttering, UPVC fascia, soffit and windows, brick walls, concrete floor. Presumed due to height restriction | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | External |  | E01 | External - external (E01) - wall panels - cement | Chrysotile | Slate tiles to roof, plastic guttering, UPVC windows, brick walls, concrete floor | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | CV1 - Ceiling Void | Ground floor - ceiling void (CV1) - limited access due to multiple layers of suspended ceiling and height | No access | Cement panels to ceiling, solid and plasterboard walls, modern ceiling tiles to floor | Further investigation required | N/A |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | CV1 - Ceiling Void | Ground floor - ceiling void (CV1) - roof panels - cement | Crocidolite (or unknown) | Cement panels to ceiling, cold and plasterboard walls, modern ceiling tiles to floor. Presumed due to height and multiple layers of suspended ceiling tiles prohibiting access | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | G015 - Boiler Room | Ground floor - boiler room (G015) - limited access due to height and pipework - Limited Access | Inaccessible (presumed) | Cement panels to ceiling, solid and plasterboard walls, boiler | Further investigation required | N/A |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | G015 - Boiler Room | Ground floor - boiler room (G015) - Roof panels - cement | Crocidolite (or unknown) | Cement panels to ceiling, solid and plasterboard walls, boiler. Presumed due to height and pipework prohibiting access | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Basement |  | B004 - Comms Room | Basement - comms room (B004) - cable wrap - rope | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, supalux panel to side of door, modern electrics. Presumed as electrics still live | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Basement |  | B004 - Comms Room | Basement - comms room (B004) - main inlet box - rope | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, supalux panel to side or door, modern electrics. Presumed as electrics still live. | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Basement |  | G001 - Boiler Room | Basement - boiler room (G001) - cable wrap -rope | Chrysotile | Supaluxceiling, sold walls, concrete floor, metal pipework with mmmg insultation, boiler, hot water cylinder, supalux panels ot metal ventilation ducting, metal flue pipe. Presumed as electrics still live. | Manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Basement |  | G001 - Boiler Room | Basement - boiler room (G001) - door header panel - cement | Chrysotile | Supaluxceiling, solid walls, concrete floor, metal pipework with mmmf insulation, boiler, hot water cylinder, supalux panels to metal ventilation ducting, metal flue pipe | Encapsulate, label, and manage | D |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | G000b - Cupboard | Ground floor - cupboard (G000b) - inaccessible | Inaccessible (presumed) | Nobody knew the code | Further investigation required | N/A |
| 2151 | London | Newham | 29 Romford Road | 29 Romford Road | 29 Romford Road, Stratford, London E15 4LY | Ground Floor |  | G029b - Cupboard | Ground floor - cupboard (G029b) - inaccessible | Inaccessible (presumed) | Door locked; no keys available | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G009 - Consultants Room | Ground floor - consultants room (G009) - inaccessible | Inaccessible (presumed) | Locked at the time of survey, no key available | Further Investigation Required Prior to Works | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G011 - Consultants Room | Ground Floor - Consultants Room (G011) - No access below laminate flooring | Inaccessible (presumed) | Plasterboard ceiling, solid walls, laminate flooring. Due to potential damage access could cause | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G004 - Office | Ground floor - office (G004) - no access below laminate flooring | Inaccessible (presumed) | Laminate flooring, plastered walls, plasterboard ceiling. Due to potential damage access could cause | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E002 - Roof Area | External - roof areas (E002) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G003 - Electrical Cupboard | Ground floor - electrics cupboard (G003) - inaccessible | Inaccessible (presumed) | Solid ceiling walls and floor. Modern electrics | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G012 - Cleaners Cupboard | Ground floor - cleaners cupboard (G012) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS001 - Loft Space | Roof Void - loft space (LS001) - inaccessible | Inaccessible (presumed) | Inaccessible due to tenants activity. | Further investigation required | N/A |
| 2144 | London | Newham | 117 Balaam Street | 117 Balaam Street | 117 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E002 - Roof Area | Roof areas (E002) - roof tiles | Chrysotile | Imitation slate tiles to roof, metal and plastic rainwater goods, wood soffits and facias. Presumed due to height | Manage | D |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G003 - Stair Lobby | Ground Floor - Stair Lobby (G003) - No access below carpeted flooring | Inaccessible (presumed) | Carpet laid on laminate, plastered and plasterboard walls, plasterboard ceiling. Timber stairs with carpetted treads Unable to access under the laminate due to potential damage access could cause | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G01 - Entrance Lobby | Ground floor - entrance lobby (G01) - no access below laminate flooring | Inaccessible (presumed) | Vinyl flooring laid on laminate, plastered and plasterboard walls, plasterboard ceiling. Unable to access under the laminate due to potential damage access could cause | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G02 - Team Room | Ground floor - team room (G02) - no access below laminate flooring | Inaccessible (presumed) | Vinyl flooring laid on laminate, plastered walls, plasterboard ceiling. Unable to access under the laminate due to potential damage access could cause | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G08 - Cupboard off waiting area | Ground floor - cupboard off waiting area (G08) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Ground Floor |  | G09 - Electrical Cupboard | Ground floor - electric cupboard (G09) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof void - loft space (LS01) - inaccessible | Inaccessible (presumed) | Felt to ceiling, timber beams, block walls, mmmf insulation. Limited access due to lack of floor boards | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E001 - Roof areas | External - roof areas (E001) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | First Floor |  | F09 - Cupboard | First floor - cupboard (F09) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof void - Loft space (LS01) - ceiling - bitumen felt | Chrysotile | Felt to ceiling, timber beams, block walls, mmmf insulation. Presumed due to acess issues | Manage | D |
| 2145 | London | Newham | 119 Balaam Street | 119 Balaam Street | 119 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E001 - Roof areas | External - roof areas (E001) - roof tiles | Chrysotile | Imitation slate tiles to roof, metal and plastic rainwater goods, wood soffits and facias | Manage | D |
| 2146 | London | Newham | 121 Balaam Street | 121 Balaam Street | 121 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof Void - Loft Space (LS01) - - All Areas | Inaccessible (presumed) | Felt to ceiling, timber beams, block walls, mmmf insulation, plastic water tank. Visual inspection from hatch due to limited access. Inaccessible due to tenants activity. | Further investigation required | N/A |
| 2146 | London | Newham | 121 Balaam Street | 121 Balaam Street | 121 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E002 - Roof Area | External - roof areas (E002) - inaccessible | Inaccessible (presumed) | No access | Further investigation required | N/A |
| 2146 | London | Newham | 121 Balaam Street | 121 Balaam Street | 121 Balaam Street, Plaistow, London, E13 8AF | Roof |  | LS01 - Loft Space | Roof void - loft space (LS01) - roof felt | Chrysotile | Felt to ceiling, timber beams, block walls, mmmf insulation, plastic water tank. Visual inspection from hatch due to limited access. Presumed due to access issues | Manage | D |
| 2146 | London | Newham | 121 Balaam Street | 121 Balaam Street | 121 Balaam Street, Plaistow, London, E13 8AF | Roof |  | E002 - Roof Area | External - roof areas (E002) - roof tiles | Chrysotile | Imitation slate tiles, metal and plastic rain water goods, wood soffits and facias. Presumed due to height | Manage | D |
| 2141 | London | Newham | 385 Barking Road | 385 Barking Road | 385 Barking Road, London E13 8AL | Basement |  | 00579 - Comms Room | Basement - Comms room (00579) - Electrical intake - Textile wrap | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor Presumed due to live electrics | Manage | D |
| 2141 | London | Newham | 385 Barking Road | 385 Barking Road | 385 Barking Road, London E13 8AL | Basement |  | 00577 - Electrical Cupboard | Basement - electrical cupboard (00577) - inaccessible | Inaccessible (presumed) | No key available | Further investigation required |  |
| 2141 | London | Newham | 385 Barking Road | 385 Barking Road | 385 Barking Road, London E13 8AL | Basement |  | 00584 - Cupboard | Basement - cupboard (00584) - - All areas | Inaccessible (presumed) | Plasterboard ceiling, plasterboard and solid walls, carpet to concrete floor. Limited access due to stored items. | Further investigation required | N/A |
| 2141 | London | Newham | 385 Barking Road | 385 Barking Road | 385 Barking Road, London E13 8AL | Basement |  | 00577 - Electrical Cupboard | Basement - Electrical cupboard (00577) - Electrical intake - Textile wrap | Chrysotile | Plasterboard board, solid and plasterboard walls, carpet over concrete floor, wooden boards behind modern electrics. Presumed due to live equipment | Manage | D |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Basement |  | B01 - Boiler room | Basement - Boiler room (B01) - Cable wrap - Rope | Chrysotile | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation, boilers Presumed as electrics still live | Manage | N/A |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Basement |  | B01 - Boiler room | Basement - Boiler room (B01) - Wall mounted electrics - Textile internals | Chrysotile | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation, boilers | Manage | D |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Basement |  | B01 - Boiler room | Basement - boiler room (B01) - pipework - residue | Fibrous anthophyllite | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation, boilers | Remove | N/A |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Basement |  | B01 - Boiler room | Basement - boiler room (B01) - walls - residue | Chrysotile + Anthophyllite | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation, boilers | Remove | N/A |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Ground Floor |  | G12 - Clinic Room | Ground floor - clinic room (G12) - inaccessible | Inaccessible (presumed) | Clinic in session | Further investigation required |  |
| 2142 | London | Newham | 409 Stratford High Street | 409 Stratford High Street | 409 Stratford High Street, London E15 4QZ | Ground Floor |  | G18 - Comms Room | Ground floor - comms room (G18) - inaccessible | Inaccessible (presumed) | No key available | Further investigation required |  |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Sixth Floor |  | Plant Room | Sixth floor - plant room (1) - joints to ducting - mastic | Chrysotile | Concrete floor, block walls, profiled steel sheet roof. Armorflex covered MMMF insulation to pipes, tanks, and ducting | Manage | D |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Roof |  | Roof Areas | External - roof areas (1) - air con ducting joints - mastic | Chrysotile | Concrete covered with stones and concrete slabs. Metal and composite tile cladding to parapet | Manage | D |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Sixth Floor |  | 3 - Lift Motor Room | Sixth floor - lift motor room (3) - lift geat (both lifts) - cement brake shoes | Chrysotile | Concrete floor, block walls, profiled steel sheet roof. Armorflex covered MMMF insulation to pipes, tanks, and ducting | Manage | D |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | First Floor |  | 12 - Boardroom | First floor - boardroom (12) - inaccessible | Inaccessible (presumed) | No access | Further investigation required |  |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Ground Floor |  | 13 - Office 2 | Ground floor - office 2 (13) - inaccessible | Inaccessible (presumed) | No access | Further investigation required |  |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Basement |  | 1 - Plant Room | Basement - plant room (1) - pipe to side of tank - gaskets (2) | Chrysotile | Concrete floor, brick and block walls, profiled steel sheet roof. Foil faced MMMF insulation to pipes and tank | Manage | D |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Basement |  | 16 - Electricity Sub-Station | Basement - electricity sub-station (16) - inaccessible | Inaccessible (presumed) | UK Power Networks access only | Further investigation required |  |
| 2159 | London | Trust wide | 9 Alie Street | 9 Alie Street | 9 Alie Street, London, E1 8DE | Basement |  | 18 - Comms Room | Basement - comms room (18) - inaccessible | Inaccessible (presumed) | No access | Further investigation required |  |
| 2147 | London | Newham | Appleby Health Centre | Appleby Health Centre | Appleby Health Centre, 63 Appleby Road, Canning Town, London E16 1LQ | Lift Shaft |  | LS001 - Lift Shaft | Lift shaft - lift shaft (LS001) - inaccessible | Inaccessible (presumed) | No lift engineer on site | Further investigation required | N/A |
| 2147 | London | Newham | Appleby Health Centre | Appleby Health Centre | Appleby Health Centre, 63 Appleby Road, Canning Town, London E16 1LQ | Ground Floor |  | G058 - Health Visitors and School Nurses Room | Ground Floor - Health Visitors and School Nurses Room (unused) (G058) - No suspect materials found | No Material Found | Plasterboard ceiling, plasterboard and solid walls, carpet to concrete floor. | No Action Required | N/A |
| 2147 | London | Newham | Appleby Health Centre | Appleby Health Centre | Appleby Health Centre, 63 Appleby Road, Canning Town, London E16 1LQ | Ground Floor |  | G045 - Store | Ground floor - store (G045) - inaccessible | Inaccessible (presumed) | No access | Further investigation required |  |
| 2147 | London | Newham | Appleby Health Centre | Appleby Health Centre | Appleby Health Centre, 63 Appleby Road, Canning Town, London E16 1LQ | Ground Floor |  | G050A - Meeting Room Store | Ground Floor - Meeting Room Store (G050A) - No suspect materials found | No Material Found | Plasterboard ceiling and walls, fibreboard panels behind sink. Carpet to concrete floor. | No Action Required | N/A |
| 2147 | London | Newham | Appleby Health Centre | Appleby Health Centre | Appleby Health Centre, 63 Appleby Road, Canning Town, London E16 1LQ | Ground Floor |  | G051A - Group 1 Store | Ground Floor - Group Room 1 Store (G051A) - No suspect materials found | No Material Found | Plasterboard ceiling, plasterboard walls, carpet to concrete floor. | No Action Required | N/A |
| 2125 | London | City & Hackney | Donald Winnicott Centre | Donald Winnicott Centre | South Hackney CMHT, Donald Winnicott Centre, Coate Road, London, E2 9AG | Lift Shaft |  | 1 - Lift Shaft | Lift shaft (1) - inaccessible | Inaccessible (presumed) | No access due to no lift engineer on site. | Further investigation required | N/A |
| 2125 | London | City & Hackney | Donald Winnicott Centre | Donald Winnicott Centre | South Hackney CMHT, Donald Winnicott Centre, Coate Road, London, E2 9AG | Third Floor |  | 1 - Tank / Lift Motor Room | Third floor - tank/lift motor room (1) - lift machinery - brake pads | Chrysotile | Strummit board ceiling. Timber/plastic walls. Concrete floor. Timber upstands. Plastic tank.metal flue. Due to age and appearance | Manage | D |
| 2125 | London | City & Hackney | Donald Winnicott Centre | Donald Winnicott Centre | South Hackney CMHT, Donald Winnicott Centre, Coate Road, London, E2 9AG | Basement |  | 6 - Boiler Room | Basement- boiler room (6) - pipework flanges to calorifier - gaskets | Chrysotile | Concrete ceiling. Solid walls. Quarry tiled floor. Metal pipework. MMMF insultation. Modern boilers and flue. Presumed due to age and appearance | Manage | D |
| 2125 | London | City & Hackney | Donald Winnicott Centre | Donald Winnicott Centre | South Hackney CMHT, Donald Winnicott Centre, Coate Road, London, E2 9AG | Roof |  | 2 - External | External (2) - damp proof course - Bitumen | Chrysotile | Brick walls. Flat roof. Timber windows | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - waiting room (1) - above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - BBV room (2) - in concrete above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - BBV room (2) - debris to timber above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - group activity room (3) - debris to timber above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under moden lino. Meeting in session | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - BBV room (2) - flue pipe behind timber and plastic panels - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - disabled WC (4) - above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - mens WC (5) - to timber and concrete above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - ladies WC (6) - to timber and concrete above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor under modern lino | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - admin office (7) - debris above suspended ceiling tiles - insulation board | Chrysotile + Amosite | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Remove | B |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - admin office (7) - flue pipe behind timer and plastic panels - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - staff office (8) - flue pipe behind timer and plastic pabels - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - suite 3 (9) - flue pipe behind timber and plastic panels - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboar walls, concrete floor. Meeting in session | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - interview room 3 (10) - flue pipe behind timer and plastic panels - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - service duct (11) - cement collar in floor - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Manage | D |
| N/A | N/A | N/A | Ilford Chambers | N/A | N/A | Third Floor |  |  | Third floor - service duct 2 (12) - flue pipe - cement | Chrysotile | Modern ceiling tiles suspended on metal framework with concrete ceiling above, solid and plasterboard walls, concrete floor | Manage | D |
| 2154 | London | Forensics | John Howard Centre | Elizabeth Fry Building | Elizabeth Fry Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | Lift Shaft |  | LS1 - Lift Shaft 1 | Lift shaft - lift shaft (LS1) - inaccessible | Inaccessible (presumed) | No lift engineer on site | Unable to access |  |
| 2152 | London | Forensics | John Howard Centre | John Warburton | John Warburton Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | Lift Shaft |  | LS1 - Lift Shaft 1 | Lift shaft - lift shaft 1 (LS1) - inaccessible | Inaccessible (presumed) | No lift engineer on site | Unable to access |  |
| 2152 | London | Forensics | John Howard Centre | John Warburton | John Warburton Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | Lift Shaft |  | LS1 - Lift Shaft 2 | Lift shaft - lift shaft 2 (LS1) - inaccessible | Inaccessible (presumed) | No lift engineer on site | Unable to access |  |
| 2152 | London | Forensics | John Howard Centre | John Warburton | John Warburton Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | First Floor |  | F92 - Store Room | First floor - store room (F92) - inaccessible | Inaccessible (presumed) | Door locked, no key available | Unable to access |  |
| 2152 | London | Forensics | John Howard Centre | John Warburton | John Warburton Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | Ground Floor |  | G83 - Store Room | Ground floor store room (G83) - limited access | Inaccessible (presumed) | Timber ceiling, solid walls, concrete floor. Stored items, limited access | Unable to access |  |
| 2153 | London | Forensics | John Howard Centre | Whitbread Building | Whitbread Building, John Howard Centre, 12 Kenworthy Road, London, E9 5TD | Basement |  | 13 - Lift Motor Room | Basement - lift motor room (13) - lift motor - brake pads | Chrysotile | Concrete ceiling, solid walls, concrete floor | Manage | D |
| 2240 | London | Tower Hamlets | 71 Johnson Street | 71 Johnson Street | 71 Johnson Street, London E1 0AQ | Ground Floor |  | 2 - Understairs Cupboard | Ground floor - understairs cupboard (2) - inaccessible | Inaccessible (presumed) | Access blocked due to stored items in front of the cupboard. | Further investigation required prior to works | N/A |
| 2148 | London | Newham | Joyce Campbell Clinic | Joyce Campbell Clinic | Joyce Campbell Clinic, 478 Barking Road, London, E6 2LT | Ground Floor |  | G006 - Electrical Cupboard | Ground Floor - Electrical cupboard (G006) - Electrical intake - Textile wrap | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, modern fuseboards. Presumed due to live electrics | Manage | D |
| 2148 | London | Newham | Joyce Campbell Clinic | Joyce Campbell Clinic | Joyce Campbell Clinic, 478 Barking Road, London, E6 2LT | Ground Floor |  | G006 - Electrical Cupboard | Ground Floor - Electrical cupboard (G006) - Wall mounted electrics - Textile internals | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, modern fuseboards. Presumed as electrics still live | Manage | D |
| 2148 | London | Newham | Joyce Campbell Clinic | Joyce Campbell Clinic | Joyce Campbell Clinic, 478 Barking Road, London, E6 2LT | Ground Floor |  | G011 - Boiler Room | Ground floor - boiler room (G011) - floor tiles - reinforced composite | Chrysotile | Timber fibre board ceiling, solid walls, concrete floor, boiler | Manage | D |
| 2250 | London | MHCOP | The Lodge | Cedar Ward | The Lodge, 2 Crozier Terrace, Homerton, London, E9 6AT | Ground Floor |  | 132 - Consulting Room 9 | Ground floor - consulting room 9 (132) - inaccessible | Inaccessible (presumed) | Room occuped | Further investigation required |  |
| 2250 | London | MHCOP | The Lodge | Cedar Ward | The Lodge, 2 Crozier Terrace, Homerton, London, E9 6AT | Ground Floor |  | 136 - Consulting Room 11 | Ground floor - consulting room 11 (136) - inaccessible | Inaccessible (presumed) | Room occuped | Further investigation required |  |
| 2250 | London | MHCOP | The Lodge | Cedar Ward | The Lodge, 2 Crozier Terrace, Homerton, London, E9 6AT | Ground Floor |  | 129 - Electric Cupboard | Ground floor - electric cupboard (129) - inaccessible | Inaccessible (presumed) | No one knew where the key was | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Lift Shaft |  | LS1 - Lift Shaft | Lift shaft - lift shaft (LS1) - inaccessible | Inaccessible (presumed) | No lift engineer on site | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Seventh Floor |  | F7.03 - Lift Motor Room | Seventh floor - lift motor room (F7.03) - lift motor - brake pads | Chrysotile | Concrete ceiling, solid walls, concrete floor, modern electrics, 2 x lift motors. Presumed as lifts still active and no lift engineer on site | Manage | B |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Ground Floor |  | GF50 - Advocacy Office | Ground floor - advocacy office (GF50) - inaccessible | Inaccessible (presumed) | Door locked, no keys available | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Ground Floor |  | Cashier And Safe | Ground floor - cashier and safe (GF53) - inaccessible | Inaccessible (presumed) | Door locked, no keys available | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Ground Floor |  | 01 - Gas Meter Cupboard | Ground floor - gas meter cupboard (01) - old pipework flange - gasket | Chrysotile | Concrete ceiling, metal cable trays, solid and plasterboard walls, concrete floor | Manage | D |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Ground Floor |  | Gas Meter Cupboard | Ground floor - gas meter cupboard (01) - limited access | Inaccessible (presumed) | Concrete ceiling,metal cable trays, solid and plasterboard walls, concrete floor due to stored items | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Ground Floor |  | Electrical Intake Room | Ground floor - electrical intake room (04) - flashguards - rope | Chrysotile | Concrete ceiling, solid walls, concrete floor, modern electrics | Manage | D |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Second Floor |  | F2.48a - Cupboard | Second floor - cupboard (F2.48a) - inaccessible | Inaccessible (presumed) | Door locked, no keys available | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Third Floor |  | F3.49a - Cupboard | Third floor - cupboard (F3.49a) - inaccessible | Inaccessible (presumed) | Stored items blocking door | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Fourth Floor |  | F4.34 and F4.35 - Bedroom And En-Suite | Fourth floor - bedroom and en-suite (F4.34 and F4.35) - inaccessible | Inaccessible (presumed) | Tenant not in | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Fourth Floor |  | F4.20 and F4.21 - Bedroom And En-Suite | Fourth floor - bedroom and en-suite (F4.20 and F4.21) - inaccessible | Inaccessible (presumed) | Tenant not in so not allowed access | Further investigation required |  |
| 2158 | London | Forensics | Wolfson House | Wolfson House | Wolfson House, 311 - 315 Green Lanes, London N4 2ES | Fourth Floor |  | F5.33 and F5.34 - Bedroom And En-Suite | Fourth floor - bedroom and en-suite (F5.33 and F5.34) - accessed - no suspect materials found | Inaccessible (presumed) | Tenant still asleep and would not get up | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 1 - S10 - Viewing suite 2 | Second floor - viewing suite 2 S10 (1) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | C - Low Risk |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 2 | Second floor - cupboard 2 (2) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 1 | Second floor - corridor 1 (3) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Observation Room 1 | Second floor - observation room 1 (4) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timer hatch panel giving access into crawl space filled with mmmf insulation | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Toilet 1 | Second floor - toilet 1 (5) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Kitchen | Second floor - kitchen (6) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S30 | Second floor - office S30 (7) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S33A | Second floor - office S33A (8) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S33B | Second floor - office S33B (9) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S34 | Second floor - office S34 (1) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Stairs 1 | Second floor - stairs 1 (11) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, rubber stair nosing | Manage | C - Low Risk |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S35 | Second floor - office S35 (12) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S36 | Second floor - office S36 (13) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 2 | Second floor - corridor 2 (14) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | C - Low Risk |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S27 | Second floor - office S27 (15) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S26 | Second floor - office S26 (16) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Lift Shaft |  | Lift Shaft | Lift shaft - lift shaft (1) - inaccessible | Chrysotile | No lift engineer on site | Further investigation required | N/A |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S25 | Second floor - office S25 (18) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 3 | Second floor - corridor 3 (19) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Stairs 2 | Second floor - stairs 2 (20) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodship paper to solid and plasterboard walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 4 | Second floor - corridor 4 (21) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodship paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Office S21 | Second floor - office S21 (22) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Viewing suite 3 S22 | Second floor - viewing suite 3 S22 (23) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | C - Low Risk |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | S18 - Family Therapy | Second floor - family therapy S18 (24) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 25 - Toilet 2 | Second floor - toilet 2 (25) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 5 | Second floor - corridor 5 (26) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Viewing Suite 1 S5 | Second floor - viewing suite 1 S5 (27) - ceiling - textured | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 3 | Second floor - cupboard 3 (28) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 4 | Second floor - cupboard 4 (29) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 6 | Second floor - cupboard 6 (30) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 7 | Second floor - cupboard 7 (31) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 8 | Second floor - cupboard 8 (32) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, newer fuseboard | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 6 | Second floor - corridor 6 (33) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plastterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Observation Room 2 | Second floor - observation room 2 (34) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber hatch panel giving access into crawl space filled with mmmf insultation | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | S17 - Clinical Psychology | Second floor - clinical psychology S17 (35) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paer to solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 9 | Second floor - cupboard 9 (36) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, newer fuseboard | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 37 - Corridor 7 | Second floor - corridor 7 (37) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber hatch panel giving access into crawl space filled with mmmf insultation | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | S16 - Clinical Psychology | Second floor - clinical psychology S16 (38) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 39 - Toilet 3 | Second floor - toilet 3 (39) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, soid and plasterboard walls, concrete floor under modern lino, ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 40 - Stairs 3 | Second floor - stairs 3 (40) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, soid and plasterboard walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 2 - Kitchen | First floor - kitchen (2) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F27 | First floor - office F27 (3) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Cupboards 1 | First floor - cupboards 1 (4) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 5 - Stairs 4 | First floor - stairs 4 (5) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, rubber stair nosing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 2 - Stairs 4 | Ground floor - stairs 4 (2) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under quarry tiles, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F14 | First floor - office F14 (6) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F15 | First floor - office F15 (7) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F16 | First floor - office F16 (8) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 9 - Corridor 1 | First floor - corridor 1 (9) - ceiling - textured coating | Chrysotile | Plasterboard ceiling and concrete ceiling above modern suspended ceiling tiles, metal pipework with mmmf insulation, solid and plasterboard walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 10 - Front Door Team F17 | First floor - front door team F17 (10) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing, timber panels to ceiling | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F21 | First floor - office F21 (11) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and platerboard walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F23 | First floor - office F23 (12) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 13 - Stairs 1 | First floor - stairs 1 (13) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F24 | First floor - office F24 (14) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Small meeting Room | First floor - small meeting room F25 (16) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F26 | First floor - office F26 (17) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F28 | First floor - office F28 (18) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 21 - Lobby | First floor - lobby (21) - ceiling - textured coating | Chrysotile | Plasterboard ceiling and concrete ceiling above modern suspended ceiling tiles, metal pipework with mmmf insulation, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F29 | First floor - office F29 (22) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F10 | First floor - office F10 (24) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 25 - Amht Admin F30 | First floor - AMHT admin F30 (25) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F31 | First floor - office F31 (26) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 27 - Toilet 1 | First floor - toilet 1 (27) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F7 | First floor - office F7 (28) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F8 | First floor - office F8 (29) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber panels to ceiling | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F9 | First floor - office F9 (30) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 31 - Stairs 5 | First floor - stairs 5 (31) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 3 - Stairs 5 | Ground floor - stairs 5 (3) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under quarry tiles, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Cupboards 3 | First floor - cupboards 3 (32) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 33 - Corridor 5 | First floor - corridor 5 (33) - ceiling - textured coating | Chrysotile | Plasterboard ceiling and concrete ceiling above modern suspended ceiling tiles, metal pipework with mmmf insulation, solid and plasterboard walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F32 | First floor - office F32 (34) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | F33 - Junior Doctors | First floor - junior doctors F33 (35) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F3 | First floor - office F3 (36) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Staff Toilet | First floor - staff toilet (37) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F34 | First floor - office F34 (38) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Office F2 | First floor - office F2 (39) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 40 - Stairs 3 | First floor - stairs 3 (40) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 43 - Cupboard 1 | Second floor - cupboard 1 (43) - inaccessible | Inaccessible (presumed) | Door locked, no key available | Manage |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 44 - Cupboard 5 | Second floor - cupboard 5 (44) - inaccessible | Inaccessible (presumed) | Door locked, no key available | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Lobby and Stairs | Ground floor - lobby and stairs 2 (4) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor under modern lino | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 5 - Stairs 1 | Ground floor - stairs 1 (5) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 6 - Kitchen 1 | Ground floor - kitchen 1 (6) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor under modern lino, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 7 - New Staff Room | Ground floor - new staff room (7) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor, timber boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Female Wc | Ground floor - female WC (8) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor under modern lino, ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Male Wc | Ground floor - male WC (9) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor under modern lino ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 10 - Corridor 1 | Ground floor - corridor 1 (10) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, timber panels to ceiling | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Bookable Room | Ground floor - bookable room (11) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid and plasterboard walls, concrete floor, plasterboard boxing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Prayer and Reflection Room | Ground floor - prayer and reflection room (12) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, woodchip paper to solid and plasterboard walls, concrete floor | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Corridor 2 | Ground floor - corridor 2 (16) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Lobby 1 | Ground floor - lobby 1 (17) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor under modern lino | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Reception | Ground floor - reception (19) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor under modern lino | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | G4- Client Waiting Room | Ground floor - client waiting room G4 (20) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor under modern lino | Encapsulate, label and manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Corridor 3 | Ground floor - corridor 3 (21) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 24 - Lobby 2 | Ground floor - lobby 2 (24) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, timber panels to ceiling | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Male Wc 2 | Ground floor - male WC 2 (25) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Female Wc 2 | Ground floor - female WC 2 (26) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern, timber panel to ceiling | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Store G18 | Ground floor - store G18 (27) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, modern fuseboard, hot water cylinder | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 27 - Store G18 | Ground floor - store G18 (27) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid walls, concrete floor, modern fuseboard, hot water cylinder | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 28 - Toiler And Shower G19 | Ground floor - toiler and shower G19 (28) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor under modern lino, ceramic cistern | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Cupboard 3 | Ground floor - cupboard 3 (29) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Cupboard 3 | Ground floor - cupboard 3 (29) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 30 - Kitchen 2 | Ground floor - kitchen 2 (30) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid walls, concrete floor under modern lino, timber panels to ceiling | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Corridor 4 | Ground floor - corridor 4 (31) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Office G21 | Ground floor - office G21 (32) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 33 - Cupboard 4 | Ground floor - cupboard 4 (33) - in accessible | Inaccessible (presumed) |  | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | G23 - Admin Room | Ground floor - admin room 2 G23 (34) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | G16 - Filing room | Ground floor - filing room G16 (35) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor, timber panels to ceiling | Manage | C - Low Risk |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | G8 - Admin Room | Ground floor - admin room 1 G8 (36) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 37 - Stairs 3 | Ground floor - stairs 3 (37) - ceiling - textured coating | Chrysotile | Plasterboard and concrete ceiling, solid walls, concrete floor, rubber stair nosing | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Comms Room | Ground floor - comms room (38) - ceiling - textured coating | Chrysotile | Plasterboard, solid walls, concrete floor under modern lino | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 39 - Electrics Room | Ground floor - electrics room (39) - floor tiles - reinforced composite | Chrysotile | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 39 - Electrics Room | Ground floor - electrics room (39) - fuseboard - flashguards | Chrysotile | Concrete ceiling, solid walls, concrete floor, metal pipework with mmmf insulation. Presumed as electrics still live | Manage | C |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  |  | Ground floor - large meeting room (43) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Large meeting Room | Ground floor - large meeting room (43) - floor tiles - reinforced composite | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor. Under carpet | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Archives G33 | Ground floor - archives G33 (44) - ceiling - textured coating | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | G33 - Archives G | Ground floor - archives G33 (44) - floor riles - reinforced composite | Chrysotile | Plasterboard ceiling, woodchip paper to solid walls, concrete floor. Under carpet | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 45 - Storeage G35 | Ground floor - storeage G35 (45) - floor tiles - reinforced composite | Chrysotile | Concrete ceiling, solid walls, concrete floor, metal pipework and heating ducting. Under carpet | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 46 - Office/Self Contained Flat | Ground floor - office/self contained flat (46) - ceiling - textured coating | Chrysotile |  | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 47 - Wc | Ground floor - WC (47) - ceiling - textured coating | Chrysotile |  | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | 44 - Store F22 | First floor - store F22 (44) - inaccessible | Inaccessible (presumed) | Door locked, no key available | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | 45 - Store | Second floor - store (45) - inaccessible | Inaccessible (presumed) | Door locked, no key available | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Cupboard 1 | Second floor cupboard 1 (43) under carpet tiles | Chrysotile | Textured coating to ceiling, solid and plasterboard walls, tiles under carpet floorings | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | S10 - Viewing Suite 2 | Second floor - viewing suite 2 S10 - under carpet floor tiles | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Second Floor |  | Corridor 1 | Second floor corridor 1 (3) - under carpet floor tiles | Chrysotile | Plasterboard ceiling, solid and plasterboard walls, concrete floors | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Roof |  | 1 - Loft Space Above Cupboard 1 | Roof void - loft space above cupboard 1 (1) - all areas |  | Timber ceiling and beams. Visual inspection from hatch was restricted due to the side of the hatch. Limited access due to hatch size | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | First Floor |  | Store Room | First foor - store room (45) - ceiling - textured coating |  | Textured coating to ceiling, tiled walls, vinyl flooring to solid floor | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 48 - Waiting Room Cupboard | Ground floor - waiting room cupboard (48) - inaccessible |  | Locked, no key availale | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 49 G25 | Ground floor G25 (49) - inaccessible |  | Locked, no key availale | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Water tank / Electrical Store | Ground floor - water tank / electrical store (50) - ceiling - textured coating |  | Textured coating to ceiling, plasterboard and solid walls, vinyl floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Water tank / Electrical Store | Ground floor - water tank / electrical store (50) - ceiling - all areas |  | Textured coating to ceiling, plasterboard and solid walls, vinyl floor. Limited access due to stored items | Further investigation required |  |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | Staff Room Cupboard | Ground floor - staff room cupboard (51) - ceiling - textured coating |  | Textured coating to ceilng, plasterboard walls, carpet to solid floor | Manage | D |
| 2140 | London | Newham | York House | York House | York House, 411 Barking Road, London, E13 8AL (plus 409 - single room) | Ground Floor |  | 33 - Cupboard 4 | Ground Floor - Cupboard 4 (33) - Floor below fitted carpet - Tiles and adhesive | Chrysotile (presumed) | Solid walls, floor and ceiling with a fitted carpet present. | Manage | D |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | G.01 | Ground floor / G.01 | Amosite | Insulating board panel above door in ceiling void | Encapsulate | Medium |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | G.01 | Ground floor / G.01 | Amosite | Insulating board debris in ceiling void | Remove | Medium |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | G.01 | Ground floor / G.01 | Amosite | Insulating board panel between timber floor and timber joist | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | Post Room | Ground floor / Post Room | Amosite | Insulating board panel above metal beam | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | Post Room | Ground floor / Post Room | Chrysotile | Floor tiles and adhesive floor in cupboard | Manage | Very Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | Fire Exit | Ground floor / Fire Exit | Chrysotile | Textured coated ceiling | Manage | Very Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | Fire Exit | Ground floor / Fire Exit | Chrysotile | Floor tiles and adhesive floor | Manage | Very Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Ground Floor |  | Old Plant Room | Ground floor / old plant room | Chrysotile | Gaskets to pipe flange | Manage | Very Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Second Floor |  | WC | 2nd floor / WC | Chrysotile | Rope seal to ducting | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Fifth Floor |  | WC | 5th floor / WC | Chrysotile | Rope seal to ducting | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Sixth Floor |  | WC | 6th floor / WC | Chrysotile | Rope seal to ducting | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Seventh Floor |  | WC | 7th floor / WC | Chrysotile | Rope seal to ducting | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Eighth Floor |  | WC | 8th floor / WC | Chrysotile | Rope seal to ducting | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Boiler Room | 10th floor / Boiler Room | Chrysotile | Gaskets to boilers | Manage | Very Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Boiler Room | 10th floor / Boiler Room | Amosite | Insulating board inside door | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Boiler Room | 10th floor / Boiler Room | Chrysotile | Rope seal to boilers | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Boiler Room | 10th floor / Boiler Room | Chrysotile | Textile gasket to rear of boilers | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Lift Motor Room | 10th floor / Lift Motor Room | Amosite | Insulating board inside door | Manage | Low |
| 2173 | Luton and Beds | Luton | Charter House | Charter House | Charter House, Alma Street, Luton LU1 2PL | Tenth Floor |  | Lift Motor Room | 10th floor / Lift Motor Room | Chrysotile | Rope seal to ducting | Manage | Low |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | External |  | Entry Canopy | External - textiles/ropes within fabric of entry canopy | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Low |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | Roof |  | Onto Roof | External - onto roofs |  | Inaccessible | Inspect prior to disturbance |  |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | Basement |  | Boiler Room | Basement 1 / basement boiler room - lagging debris within sealed aperture | Crocidolite (or unknown) | Usually inaccessible or unlikely to be disturbed | Manage | High |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | Basement |  | Boiler Room | Basement 1 / basement boiler room - within fabric of boilers boiler room |  |  | Inspect prior to disturbance |  |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | Ground Floor |  | 9 | Ground floor / 9 - within electrics boxes/installations |  |  | Inspect prior to disturbance |  |
| 2180 | Luton and Beds | Beds | 29 Barford Avenue | 29 Barford Avenue | Barford Avenue, 29 Barford Avenue, Bedford, MK42 0DS | Ground Floor |  | 20 | Ground floor / 20 - within loft via hi-level hatch |  |  | Inspect prior to disturbance |  |
| 2181 | Luton and Beds | Luton | Beacon House | Beacon House | Beacon House, 5 Regent Street, Dunstable, LU6 1LR | Ground Floor |  | G.15 | Ground floor / G.15 - internal lining to safe |  | Inaccessible | Inspect prior to disturbance |  |
| 2181 | Luton and Beds | Luton | Beacon House | Beacon House | Beacon House, 5 Regent Street, Dunstable, LU6 1LR | Ground Floor |  | G.19 | Ground floor / G.19 |  | Inaccessible | Inspect prior to disturbance |  |
| 2182 | Luton and Beds | Luton | Beech Close | Resource Centre | Beech Close Resource Centre, 5 Beech Close, Dunstable, LU6 3SD | External |  | Electrical Room | External - within electrical room |  | Inaccessible | Inspect prior to disturbance |  |
| 2182 | Luton and Beds | Luton | Beech Close | Resource Centre | Beech Close Resource Centre, 5 Beech Close, Dunstable, LU6 3SD | Ground Floor |  | Corridor 2 | Ground floor / corridor 2 - lift and lift shaft |  | Inaccessible | Inspect prior to disturbance |  |
| 2176d | Luton and Beds | Luton | Calnwood Road | Evergreen Ward | Evergreen Ward, 1st Floor Calnwood Road, Luton LU4 0LU | Ground Floor |  | Lift and Lift Shaft | Ground floor - lift and lift shaft |  | Inaccessible | Further investigation required prior to works |  |
| 2184 | Luton and Beds | Beds | Bedford Health Village | Cedar House | Cedar House, Bedford Health Village, 3 Kimbolton Road, Bedford, MK40 2NT | Ground Floor |  | 0.17 - Kitchent | Ground floor / 0.17 kitchen | Crocidolite (or unknown | Usually inaccessible or unlikely to be disturbed | Manage | Medium |
| 2184 | Luton and Beds | Beds | Bedford Health Village | Cedar House | Cedar House, Bedford Health Village, 3 Kimbolton Road, Bedford, MK40 2NT | Ground Floor |  | 0.13 | Ground floor / 0.13 - no access within electrics throughout building |  | Inaccessible | Inspect prior to disturbance |  |
| 2184 | Luton and Beds | Beds | Bedford Health Village | Cedar House | Cedar House, Bedford Health Village, 3 Kimbolton Road, Bedford, MK40 2NT | Ground Floor |  | 0.01 | Ground floor / 0.01 - no access within electrics |  | Inaccessible | Inspect prior to disturbance |  |
| 2184 | Luton and Beds | Beds | Bedford Health Village | Cedar House | Cedar House, Bedford Health Village, 3 Kimbolton Road, Bedford, MK40 2NT | Ground Floor |  | Boiler Room | Ground floor / boiler room - no access within electrics |  | Inaccessible | Inspect prior to disturbance |  |
| 2185 | Luton and Beds | Luton | Crombie House | Crombie House | Crombie House, 36 Hockliffe Street, Leighton Buzzard, LU7 8HE | External |  |  | External - cement undercloaking | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2185 | Luton and Beds | Luton | Crombie House | Crombie House | Crombie House, 36 Hockliffe Street, Leighton Buzzard, LU7 8HE | Ground Floor |  | Kitchen | Ground floor / kitchen - floor tiles with adhesive to floor | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Roof |  |  | External - roof tiles perimeter roof fascias | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 5 | Ground floor / 5 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 3 | Ground floor / 3 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Reception | Ground floor / reception - textured coating to cupboard ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 6 | Ground floor / 6 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 12 | Ground floor / 12 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Beige | Ground floor / 12 - beige vinyl/adhesive to floor | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | And | Ground floor / 8 and 13 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 8 and 13 | Ground floor / 8 and 13 - beige vinyl tiles/adhesive to floor | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Open Corridor | Ground floor / open corridor areas inc staff entry | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 7 | Ground floor / 7 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 11 | Ground floor / 11 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Textured | Ground floor / lobby - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 25 | Ground floor / 25 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 24 | Ground floor/ 24 incl store - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 23 | Ground floor / 23 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Textured | Ground floor / corridor - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 20 | Ground floor / 20 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 21 | Ground floor / 21 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 21 | Ground floor / 21 - beige vinyl tiles/adhesive to floor | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 22 | Ground floor / 22 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 22 | Ground floor / 22 - beige vinyl tiles/adhesive to ceiling | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 19 | Ground floor / 19 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 18 | Ground floor / 18 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 17 | Ground floor / 17 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 17 | Ground floor / 17 - beige vinyl tiles/adhesive to floor | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 16 | Ground floor / 16 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 16 | Ground floor / 16 - beige vinyl tiles/adhesive to ceiling | Chrysotile | Easily disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 15 | Ground floor / 15 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | 15 | Ground floor / 15 - textured coating to ceiling | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2188 | Luton and Beds | Beds | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre | EMPOWA Wellbeing Centre, 3 Woburn road, Bedford, MK40 1EG | Ground Floor |  | Boiler Room | Ground floor / boiler room | Chrysotile | Occasionally likely to be disturbed | Manage | Very Low |
| 2621 | Luton and Beds | Beds | Mountbatten House | Mountbatten House | Mountbatten House, 56/60 High Street South, Dunstable, LU6 3HD |  |  | G.09 | G.09 electrical intake cupboard |  | Presumed woven flashpads within live electrical boxes |  | Very low |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Ground Floor |  | 18 | Ground floor / 018 |  | No access within timber risers - throughout floor | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Ground Floor |  | 13 | Ground floor / 013 |  | No access within electrics | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | First Floor |  | 4 | 1st floor / 004 |  | No access within timber boxing throughout floor | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Second Floor |  | 20 | 2nd floor / 020 |  | No access within timber boxing | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Second Floor |  | 20 | 2nd floor / 020 |  | No access within water heater | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Second Floor |  | 5 | 2nd floor / 005 |  | No access within timber boxing | Inspect prior to disturbance |  |
| 2193 | Luton and Beds | Beds | Rush Court | Rush Court 5-7 | Rush Court 5-7 , Off Grove Place, Bedford, MK42 3JT | Second Floor |  | 11 | 2nd floor / 011 |  | No access within timber boxing | Inspect prior to disturbance |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | External |  |  | External - cowl top of chimney | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Roof |  |  | External - roof tiles | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Basement |  | Cellar | Basement 1 / cellar - insulating wrap to mains power cable | Chrysotile | Occassionally likely to be disturbed | Manage |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Ground Floor |  | G.01 | Ground floor / G.01 - insulating wrap to mains power cable | Chrysotile | Occassionally likely to be disturbed | Manage |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Ground Floor |  | G.13 | Ground floor / G.13 |  | No access to safe | Inspect prior to disturbance |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Roof |  | Loft space | Roof void / loft space - sarking felt behind timber roof joists within loft space | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage |  |
| 2196 | Luton and Beds | Beds | 21 The Crescent | 21 The Crescent | The Crescent, 21 The Crescent, Bedford, MK40 3JJ | Roof |  | Loft space | Roof void / loft space - flu stack within in loft space | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Roof |  | 15 | External 0015 - cement undercloaking eave sections of roof throughout site externally | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Roof |  | 17 | External 0017 - cement undercloaking external sheds 022/023 roofs | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Roof |  | 18 | External 0018 - cement undercloaking 1st floor eaves of roof | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Roof |  | 19 | External 0019 - cement undercloaking adj roof left hand of 'grit' alcove | Chrysotile | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 11 | Ground floor / 011 - no access within tiber riser to this room and throughout |  |  | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 12 | Ground floor / 012 - no acccess within electrics |  |  | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 12 | Ground floor / 012 - gaskets to redundant pipes/valves on floor | Chrysotile | Ocasionally inaccessible or unlikely to be disturbed | Remove | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 12 | Ground floor / 012 - lagging debruswalls/floor.ceiling.adj pipe penetrations | Chrysotile + Amosite | Ocasionally inaccessible or unlikely to be disturbed | Restrict access and remove | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 013 and 014 | Ground floor / 013 and 014 - limited access to ceiling void |  |  | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 013 and 014 | Ground floor / 013 and 014 - redundant cement tank floor of ceiling | Crocidolite (or unknown) | Usually inaccessible or unlikely to be disturbed | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 013 and 014 | Ground floor / 013 and 014 - cement panel to hatch ceiling | Chrysotile | Identified | Manage | Very low |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 013 and 014 | Ground floor / 013 and 014 - no access within water heater |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | No Acces | Ground floor - no acces within boiler fabric |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 22 | Ground floor / 022 - inaccessable |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 18 | Ground floor / 018 - no access within electrics |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | Ground Floor |  | 16 | Ground floor / 016 - inaccessible |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2198 | Luton and Beds | Beds | The Lawns | The Lawns | The Lawns, The Baulk, Biggleswade, SG18 0PT | First Floor |  | 6 | 1st floor / 006 - no access within void |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | Basement |  | Room | Basement 1 / plant room - lagging debris to walls | Chrysotile | Identified | Restrict access and remove | High |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | First Floor |  | 6 | 1st floor / 006 - x2 insulating boards either side of reinforced glass | Amosite | Identified | Manage | Low |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | First Floor |  | 10 | 1st floor / 010 - insulating board base panel/fillet to partition | Amosite | Strongly presumed | Manage | Low |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | First Floor |  | 13 | 1st floor / 013 - well bound material - lid/tank cistern tank | Amosite | Identified | Manage | Very low |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | First Floor |  | 27 | 1st floor / 027 - x2 insulating boards base panels to partition | Amosite | Strongly presumed | Manage | Low |
| 2200c | Luton and Beds | Beds | Twinwoods | Admin Block | Twinwoods - Admin Block, Milton Road, Clapham, Bedford, MK41 6AT | First Floor |  | 43 | 1st floor / 043 - well bound material-lid/tank cistern tank | Amosite | Strongly presumed | Manage | Very low |
| 2200f | Luton and Beds | Beds | Twinwoods | Clinical Resource Centre | Twinwoods - Clinical Resource Centre, Milton Road, Clapham, Bedford, MK41 6AT | Roof |  |  | External - bitumen roof coating roof | Chrysotile | Identified | Manage | Very low |
| 2200a | Luton and Beds | Beds | Twinwoods | Raymond Smith | Twinwoods - Raymond Smith (Specialist Medical), Milton Road, Clapham, Bedford, MK41 6AT | Roof |  | Loft | Roof void / loft - insulating board lining to loft hatch | Amosite | Identified | Encapsulate | Medium |
| 2200b | Luton and Beds | Beds | Twinwoods | Russell Block | Twinwoods - Russell Block, Milton Road, Clapham, Bedford, MK41 6AT | Roof |  | WCs / Boiler Room | External - cement corrugated roof sheets roof to WC's/boiler room | Chrysotile | Identified | Manage | Very low |
| 2200b | Luton and Beds | Beds | Twinwoods | Russell Block | Twinwoods - Russell Block, Milton Road, Clapham, Bedford, MK41 6AT | Ground Floor |  |  | Ground floor / electrics - textile/bitumen coated cable wrap to mains input | Chrysotile | Presumed | Manage | Low |
| 2200g | Luton and Beds | Beds | Twinwoods | Whitbread Centre | Twinwoods - Whitbread Centre, Milton Road, Clapham, Bedford, MK41 6AT | External |  |  | External - cement panels undercloaking to lean-to building section | Chrysotile | Identified | Manage | Very low |
| 2179 | Luton and Beds | Luton | 67 High Street | 67 High Street | 67 High Street North, Dunstable, LU6 1JD (ground floor) | Ground Floor |  | G.06 | Ground floor / G.06 |  | Inaccessible | Inspect prior to disturbance |  |
| 2179 | Luton and Beds | Luton | 67 High Street | 67 High Street | 67 High Street North, Dunstable, LU6 1JD (ground floor) | Ground Floor |  | G.32 | Ground floor / G.32 |  | Inaccessible | Inspect prior to disturbance |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.14 | G.14 - corridor |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.15 | G.15 - corridor |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.16 | G.16 - corridor |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.17 | G.17 - office |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.18 | G.18 - office | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.25 | G.25 - WC |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.26 | G.26 - WC |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.27 |  |  | Location not inspection - asbestos suspected |  |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.28 | G.28 - boiler room |  | High presumption of the presence of asbestos materials - Further investigation required |  |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.34 | G.34 - corridor | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.35 | G.35 - lobby | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.37 | G.37 - office | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.39 | G.39 - corridor | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.40 | G.40 - male wc |  |  | Removed |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.41 | G.41 - female wc |  |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.42 | G.42 - WC lobby |  |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.43 | G.43 - staff room | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.44 | G.44 - admin room | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.45 | G.45 - server room | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.46 | G.46 - office | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.48 | G.48 - reception office | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.49 | G.49 - kitchen | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.50 | G.50 - store | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.51 | G.51 - store | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.52 | G.52 - dentist room | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.53 | G.53 - dentist room | Chrysotile |  | Monitor |  |
| 2260 | London | Barking and Dagenham | Five Elms Medical Centre | Five Elms Medical Centre | Five Elms Medical Centre, Dagenham, RM9 5TT | Ground Floor |  | G.57 | G.57 - corridor | Chrysotile |  | Monitor |  |
| 2261 | London | Havering | Upminster Medical Centre | Upminster Medical Centre | Upminster Medical Centre, St Mary's Lane, Upminster RM14 3DH | Ground Floor |  |  | Ground floor/entrance waiting room | Chrysotile | Presumed | Manage | (3) Very low |
| 2261 | London | Havering | Upminster Medical Centre | Upminster Medical Centre | Upminster Medical Centre, St Mary's Lane, Upminster RM14 3DH | Ground Floor |  |  | Ground floor/corridor one | Chrysotile | Presumed | Manage | (3) Very low |
| 2256 | Luton and Beds | Primary Care (Luton) | Leighton Road Surgery | Leighton Road Surgery | Leighton Road Surgery, Leighton Road, Leighton Buzzard LU7 1LB |  |  |  | External - cement under cloaking | Chrysotile |  | Manage | (3) Very low |
| 2239 | Luton and Beds | Luton | Whichellos Cottage | Whichellos Cottage | Whichellos Cottage, The Elms, Linslade, Leighton Buzzard, LU7 2TD |  |  |  | External - no access to rear of building |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2201 | Luton and Beds | Luton | Whichellos Wharf | Whichellos Wharf | Whichellos Wharf, The Elms, Linslade, Leighton Buzzard, LU7 2TD | Ground floor |  | Ground floor / electrical intake room |  |  | Inaccessible (presumed) | Inspect prior to disturbance |  |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Basement |  | Basement - boiler room (025) - walls insulation residue | Remove if affected by the works | Chrysotile + Amosite |  |  | B |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - interview room (022) - ceiling - textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - chiropodists (021) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - treatment room (020) - ceiling - textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - reception admin (018) - ceiling - textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - circulation (019) - behind radiator boxings - textiles | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - circulation (019) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - office admin (015) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor WC (014) - Heatrae Sadia Internals - gaskets | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - store room (011) - ceiling - textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - disabled WC (010) - Heatrae Sadia Internals - gaskets | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - disabled WC (010) - behind radiator boxing - textiles | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - disabled WC (010) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor (012) - behind radiator boxing - textiles | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - kitchen (008) – Heatrae Sadia internatls - gaskets | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - kitchen (008) - ceiling - textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - cleaners cupboard (007) - Heatrae Sadia internatls - gaskets | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - visitors office (004) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - visitors office (003) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - speech therapy (002) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - admin office (001) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Basement - boiler room (025) - wall mounted electrics - textile internals | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Basement - boiler room (025) - pipework flanges - gaskets | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Basement - boiler room (025) - boilers textile internals | Remove if affected by the works | Chrysotile |  |  | D |
| 2200d | Luton and Beds | Beds | Twinwoods | Whitchurch | Twinwoods - Whitchurch, Milton Road, Clapham, Bedford, MK41 6AT | Ground floor |  | Ground floor - training room (023) - ceiling textured coating | Remove if affected by the works | Chrysotile |  |  | D |

# Appendix A: Policy Equalities Impact Assessment

This checklist must be completed for all new policies to understand any potential impact on equalities and to assure equality in service delivery and employment.

| Policy Name: | Asbestos Management Plan |
| --- | --- |
| Author: | Hadi Shukir Adam Hunt (Frankham Consultancy Group) Bevan Speariett |
| Role: | Assistant Director of Estates - Engineering, and Infrastructure Interim Senior Engineering Manager |
| Directorate: | Estates, Facilities & Capital Development |
| Date | 27/07/2023 |

- If any of the questions are answered ‘yes,’ then the proposed policy is likely to be relevant to the Trust’s responsibilities under the equalities duties. Please provide the ratifying Committee with information on why ‘yes’ answers were given and whether or not this is justifiable for clinical reasons.

- The author should consult with the Associate Director of People & Culture to develop a more detailed assessment of the Policy’s impact and, where appropriate, design monitoring and reporting systems if there is any uncertainty.

- A copy of the completed form must be submitted to the relevant committee when submitting the document for ratification.

- The ratifying committee will inform you if they perceive the impact to be sufficient that a more detailed assessment is required.

| Equalities Impact Assessment Question | Yes | No | Always give further information if you answer “YES” |
| --- | --- | --- | --- |
| - How does the attached policy/service fit into the Trusts overall aims? | Yes |  | The Plan has been created to meet the Trusts aims of providing and maintaining safe and health working conditions, equipment, and systems of work for all staff, patients, and visitors, and to provide such resources, information, training, and supervision as they need for this purpose. |
| - How will the policy/service be implemented? | Yes |  | The Plan will be communicated via the Trust’s Asbestos Safety Group and the ELFT Intranet. |
| - What outcomes are intended by implementing the policy/delivering the service? | Yes |  | Effective management and monitoring of ACMs within ELFT properties. |
| - How will the above outcomes be measured? | Yes |  | The outcomes will be measured via Audits, monitoring of compliance activities and via the ongoing Asbestos Safety Group meetings |
| - Who are they key stakeholders in respect of this policy/service and how have they been involved? | Yes |  | The key stakeholders are the Asbestos Safety Group (ASG) |
| - Does this policy/service impact on other policies or services? | Yes |  | Health and Safety Policy Infection Prevention and Control Policy Manual Asbestos Safety Policy Estates Operational Policy (due for release in 2024) |
| - If YES is that impact understood? | Yes |  | No further comments |
| - Does this policy/service impact on other agencies? |  | No | No further comments |
| - If YES is that impact understood? |  | No | No further comments |
| - Is there any data on the policy or service that will help inform the equalities impact assessment? |  | No | No further comments |
| - Are there are information gaps, and how will they be addressed/what additional information is required? |  | No | No further comments |
| Equalities Impact Assessment Questions | Yes | No | Comment |
| - Does the policy or service development have an adverse impact on any particular group? |  | No | No further comments |
| - Could the way the policy is carried out have an adverse impact on equality of opportunity or good relations between different groups? |  | No | No further comments |
| - Where an adverse impact has been identified can changes be made to minimise it? |  | No | No further comments |
| - Is the policy directly or indirectly discriminatory, and can the latter be justified? |  | No | No further comments |
| - Is the policy intended to increase equality of opportunity by permitting Positive Action or Reasonable Adjustment? If so, is this lawful? |  | No | No further comments |

# Appendix B: Policy Submission Form / Checklist

To be completed and attached to any policy or procedure submitted to the Trust Policy Group

| 1 | Details of policy |  |
| --- | --- | --- |
| 1.1 | Title of Policy: | Asbestos Management Plan |
| 1.2 | Author (job title) | Hadi Shukir (Interim Senior Engineering Manager) Tim Peters (Asbestos Independent Advisor) Bevan Speariett (Assistant Director of Estates – Engineering and Infrastructure) |
| 1.3 | Lead / Sponsor Sub Committee | - David Stevens - Director of Estates, Facilities & Capital Development - Asbestos Safety Group - Health, Safety and Security Committee |
| 1.4 | Reason for Policy | Effective management and monitoring of ACMs within ELFT properties. |
| 1.5 | Who does policy affect? | - Asbestos Safety Group - Health, Safety and Security Committee - Matrons / Lead Nurse - Ward or department managers - Clinical staff |
| 1.6 | Are national guidelines/codes of practice /best practice/ references incorporated and cited? | Yes |
| 1.7 | Has an Equality Impact Assessment been carried out? | Yes |
| 1.8 | Is this a revision of an existing policy? | Yes |
| 1.9 | If yes, have you identified the changes in the document? | Yes |
| 1.10 | Is the policy in the correct format? | Yes |
| 2 | Information Collation |  |
| 2.1 | Where was Policy information obtained from? | Legislation, guidance, and best practice as stated within this Plan |
| 3 | Policy Management |  |
| 3.1 | Is there a requirement for a new or revised management structure if the policy is implemented? | No |
| 3.2 | If YES attach a copy to this form | Not Applicable |
| 3.3 | If NO explain why | No changes to management structure |
| 4 | Consultation Process |  |
| 4.1 | Was there internal/external consultation? | Yes |
| 4.2 | List groups / Persons involved | Hadi Shukir (Interim Senior Engineering Manager) Tim Peters (Asbestos Independent Advisor) Bevan Speariett (Assistant Director of Estates – Engineering and Infrastructure) |
| 4.3 | Have internal/external comments been duly considered? | Yes |
| 4.4 | Date approved by relevant Sub-committee | Asbestos Safety Group |
| 4.5 | Signature of Subcommittee chair | David Stevens |
| 5 | Implementation |  |
| 5.1 | How and to whom will the policy be distributed? | The Plan will be displayed on the Trust’s Intranet page and will be communicated via the Trust’s Asbestos Safety Group |
| 5.2 | If there are implementation requirements such as training, please detail? | ELFT training will be identified on the Estates training matrix. Hard FM and Soft FM Suppliers will conduct their own training to ensure competency with training records provided. |
| 5.3 | What is the cost of implementation and how will this be funded? | No significant costs apart from ongoing training which will be funded through the Estate budget |
| 6 | Monitoring |  |
| 6.1 | List the key performance indicators e.g., core standards | - Audits undertaken by Asbestos Independent Advisor - InPhase reports |
| 6.2 | How will this be monitored and/or audited? | The outcomes will be measured via Audits, monitoring of compliance activities and via the Asbestos Safety Group |
| 6.3 | Frequency of monitoring/audit | - Asbestos Management Plan (as per review section) - Asbestos Safety Group (WSG) every 3 (three) months - Asbestos Surveys completed annually |

Completed by Bevan Speariett

Date policy approved by the Sponsor Committee: Asbestos Safety Group 27th March 2024 / Health, Safety and Security Committee 20th March 2024

Date policy approved by the Ratifying Committee:  Service Delivery Board 27th November 2024