# Ventilation Safety Policy

The East London NHS Foundation Trust strives to ensure equality of opportunity for all, both as a major employer and as a provider of health care. This procedural document has been equality impact assessed to ensure fairness and consistency for all those covered by it regardless of their individual differences and the results are outlined, as required.

| Version number: | 1.1 |
| --- | --- |
| Consultation Groups | Ventilation Safety Group Estates Management Team Infection Prevention & Control Committee Health, Safety & Security Committee |
| Approved by (Sponsor Group) | Infection Prevention & Control Committee Health, Safety & Security Committee Service Delivery Board |
| Date approved | 21 January 2026 |
| Ratified by: | Quality Committee |
| Date ratified: | 25 March 2026 |
| Name of originator/author: | Assistant Director of Estates – Engineering and Infrastructure |
| Executive Director lead: | Director of Estates, Facilities & Capital Development |
| Implementation Date: | March 2026 |
| Last Review Date | March 2026 |
| Next Review date: | March 2029 |

| Services | Applicable to |
| --- | --- |
| Trust wide | Yes |
| Mental Health and LD | Yes |
| Community Health Services | Yes |
| Primary care | Yes |

Version Control Summary

| Ver | Date | Author | Status | Comment |
| --- | --- | --- | --- | --- |
| 0.1 | March 2025 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Draft | Initial Policy drafted |
| 0.2 | March 2025 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Draft | First version of Policy reviewed by Ventilation Safety Group. |
| 0.3 | June 2025 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Draft | Policy submitted to and approved by Estates Management Team (EMT). |
| 0.4 | July 2025 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Draft | Submitted for approval at the Infection Prevention & Control Committee |
| 0.5 | August 2025 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Draft | Policy submitted to and approved at Trust Infection, Prevention and Control Committee |
| 1.0 | January 2026 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Final | Ratified at Trust Health, Safety and Security Committee |
| 1.1 | March 2026 | Bevan Speariett (Assistant Director of Estates Engineering and Infrastructure) | Final | Section 11.8 and Introduction updated |

Contents

Paragraph										         		         Page

1	Policy Gateway	4

2	Executive Summary	5

3	Introduction	5

4	General Policy Statement	6

5	Policy Implementation	6

6	Objectives	7

7	Scope	7

8	Definitions	7

9	Related Trust Policies & Procedures	8

10	Roles and Responsibilities	8

11	Duties / Responsibilities	9

12	Maintenance of Ventilation Systems	12

13	Remedial Works	12

14	Records	13

15	Schematics	13

16	Ventilation Spaces	13

17	Incident Reporting	13

18	Policy Review	13

19	Monitoring and Compliance	14

20	Monitoring Groups	14

21	References	15

22	Appendix A: Policy Equalities Impact Assessment	16

23	Appendix B: Policy Submission Form / Checklist	18

# Policy Gateway

Please complete the checklist and tables below to provide assurance around the Ventilation Safety Policy review process.

Ventilation Safety Policy Checklist

☒ I have involved everyone who should be consulted about this Policy/guidance ☒ I have identified the target audience for this Policy/guidance ☒ I have completed the correct template fully and properly ☒ I have identified the correct approval route for this Policy/guidance ☒ I have saved a word version of this Policy/guidance for future reviews and reference

Please set out what makes you an appropriate person to conduct this review:

I am the Assistant Director or Estates, Engineering and Infrastructure

Please set out the legislation, guidance, and best practice you consulted for this review:

Health and Safety at Work etc Act 1974 Control of Substances Hazardous to Health (COSHH) Regulations 2002 Workplace (Health, Safety and Welfare) Regulations 1992 Building Regulations Approved Documents L and F Health and Social Care Act 2008 (Regulated Activities) Regulations 2014 The Medicines Act 1968 and Human Medicines Regulations 2012 Building Act 1984 Building Safety Act 2022 Fire Safety Act 2021 Construction (Design and Management) Regulations 2015 Electricity at Work Regulations 1989 Management of Health and Safety at Work Regulations 1999 Provision and Use of Work Equipment Regulations 1998 Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013 (RIDDOR) Workplace (Health, Safety and Welfare) Regulations 1992 Regulatory Reform (Fire Safety) Order 2005 CIBSE Guidance HSG 258 (Health and Safety Executive Guidance) Controlling airborne contaminants at work – A guide to local exhaust Ventilation (LEV) Health Technical Memorandum (HTM) 03-01 Specialised Ventilation for healthcare premises. Part – A: The concept, design, specification, installation and acceptance testing of healthcare Ventilation Systems and Part – B: Operational Management and Performance Verification. Other references as detailed within this Policy document.

Please identify the key people you involved in reviewing this Policy why, and when:

The Ventilation Safety Group on 3rd March 2025 The Estates Management Team on 17th of June 2025 The Infection, Prevention and Control Committee on 13th of August 2025 The Health, Safety and Security Committee on 21st of January 2026

Summarise the key changes you have made and why:

First version of this Policy

# Executive Summary

The Policy of East London NHS Foundation Trust (the Trust) is to provide and maintain safe and healthy working conditions, equipment, and systems of work for all staff, patients, service users and visitors, and to provide such resources, information, training, and supervision as they need for this purpose. The Trust aims to do all that is reasonably practicable to manage Ventilation Systems safely and to follow the steps laid out in the following Policy to ensure staff, patients, service users and visitors are safe. It is considered essential that management and staff should work together positively to achieve an environment compatible with the provision of the highest quality services where health hazards to patients and others are minimised, so far as is reasonably practicable.

This Policy has therefore been produced in order that all employees and contractors are aware of both the Trust’s and their own responsibilities under the Health and Safety at Work Act 1974 (HSAWA), with respect to Ventilation Systems, Infrastructure and Equipment covered by statutory regulations. The Trust has adopted the Department of Health, Health Technical Memorandum (HTM 03-01 Part A and Part B). It is expected that this Policy will be adhered to by all the Trust's Employees and by all appointed service providers, contractors, in whatsoever capacity, with or without contractual agreements.

There is a requirement for East London NHS Foundation Trust (ELFT) to publish, issue and implement a Ventilation Safety Policy, which outlines the organisation and procedures required to achieve the objectives set out in those legislative and guidance documents. The aim of this Policy is to provide staff and contractors with a framework for the management of Ventilation Systems within Trust properties.

It is accepted that it is for management and staff to do all that is reasonably practicable to achieve compliance with the Health and Safety Executive, National Health Service, and other regulatory bodies with regard to Ventilation Safety in Healthcare Premises. Where appropriate, training and information and any necessary control measures will be provided by the Trust. The effectiveness of the Ventilation Safety Policy relies on close cooperation between the Estates department and all staff following the procedures established under this Policy. All persons working on Ventilation Systems must be suitably qualified and competent.

# Introduction

The Trust accepts its responsibilities under the Health and Safety at Work Act 1974 (HSAWA), the Management of Health and Safety at Work Regulations 1999 (MHSWR) and relevant Ventilation Health Technical Memorandums (HTM 03-01 Part A and Part B). The Trust is committed to the safe and efficient operation of all the Ventilation Assets and Systems for which it has a responsibility and will comply with the regulations and guidance documents referenced within this policy. This includes ensuring that adequate ventilation is provided to the Trust’s properties to reduce the transmission and impact of airborne infections affecting service users, staff and visitors.

The Trust will ensure that ventilation within its properties is adequate and ventilation systems are appropriately tested, inspected and verified to promote a safe working environment for all who come into contact with the Trust premises. Procedures relating to health and safety hazard identification and risk elimination must fully consider the performance and condition of ventilation systems in line with HTM 03-01 (Part A and Part B), other relevant guidance and statutory requirements.

The effectiveness of the Ventilation Safety Policy and its associated procedures relies on the Estates department actively assessing, monitoring and maintaining the assets and systems through the Trust’s appointed supply chain and contractors. Suitable and sufficient risk assessments and safe systems of work will be undertaken by appointed Competent Persons. Management will ensure that all employees involved in ventilation operation and maintenance are appropriately trained and competent. Management will also work in partnership with the Trust’s contractors to ensure that appropriate control measures are provided and maintained to ensure compliance with relevant legislation.

The Ventilation Safety Group will oversee the application of this Policy and any associated Ventilation Safety Plans, all of which must be compiled with as part of the Trust’s governance and assurance framework.

# General Policy Statement

The Trust accepts that the management of Ventilation Systems, Infrastructure and Equipment requires a high level of management commitment, professional competence, and adequate resources.

The Trust have therefore introduced a management system which includes.

- A clearly defined Ventilation Safety Policy.

- A structure, based on the complexity of the work, for implementing this Ventilation Safety Policy which includes an outline description of individual’s duties and responsibilities.

- Procedures for ensuring the effective administration of the Ventilation Safety Policy.

- A programme for the operation and servicing of Ventilation Systems and associated equipment.

- A means by which the Ventilation Safety Policy can be managed, implemented, monitored and reviewed.

- A programme of training to ensure the awareness of all staff on the use of Ventilation Systems and general Ventilation safety.

- Appropriate training for relevant professional and technical staff.

- A formally appointed Designated Person who has responsibility for the Ventilation Safety Policy.

- Appointment of a Senior Operational Manager (SOM) who has access to robust, service specific independent professional support which can promote and maintain the role of ‘informed client’ within the Trust.

- Establishing a Ventilation Safety Group in accordance with HTM 03-01.

The Ventilation Safety Policy demonstrates the Trust’s commitment to self-regulation and reflects the uniqueness and special needs of the Trust’s premises. The key aims of the Trust’s Ventilation Safety Policy are to.

- Recognise the importance of the subject.

- Ensure that responsibilities (both legal and managerial) are clearly defined and understood throughout the organisation.

- Direct staff to the relevant procedural documents to enable this compliance.

- Ensure that all Ventilation Systems, Infrastructure and Equipment is properly maintained and examined to meet legal requirements.

- Ensure that all Ventilation Systems, Infrastructure and Equipment perform in a safe and satisfactory manner.

# Policy Implementation

The Chief Executive Officer (CEO) and board have overall responsibility for the effective implementation, monitoring and review of Trust Policies. The responsibility for establishing the arrangements and organisation to carry out the requirements of this Ventilation Safety Policy has been delegated to the Director of Estates, Facilities & Capital Development, through onward delegated responsibility to the Assistant Director of Estates - Engineering and Infrastructure and the Trust’s Estates Manager, who will ensure that all possible steps are taken to provide a safe working environment and patient care conditions. The Trust managers and staff will provide adequate resources and do all that is reasonably practicable to achieve compliance with this Policy which provides the strategy and infrastructure for the Trust's Management and Control programme for Ventilation Systems.

The contents of this Policy shall be communicated and disseminated to the Trust’s staff via the Trust’s Intranet. The Ventilation Safety Group members are tasked with disseminating and implementing the requirements of the Policy to their respective teams / organisations.

# Objectives

The objective of this Policy is to ensure effective operation and maintenance of the Trust’s Ventilation Systems, Infrastructure and Equipment.

# Scope

This Policy applies to all Trust premises whether owned or occupied by the Trust 	under lease or other Service Level Agreements (SLA’s) and Private Finance Initiatives (PFI). Where the management of buildings / areas occupied by Trust staff and / or patients is carried out by others, the requirements of this Policy remain applicable although implementation of the site-specific risk management requirements is managed by local policies. It remains; therefore, the Trusts responsibility to ensure that the requirements of this Policy are notified to and 	complied with by all other parties described above.

These premises may be:

- Owned and occupied partly by the Trust.

- Owned and occupied exclusively by the Trust.

- Not owned by the Trust but occupied exclusively by the Trust on a permanent basis.

- Not owned by the Trust but occupied partly by the Trust on a permanent Basis.

- Not owned by the Trust but occupied partly by the Trust on a temporary or periodic basis.

This Policy relates to Trust buildings for which it is the Primary Duty Holder but does not relate to buildings for which the Trust does not have Duty Holder responsibilities. This Policy therefore does not apply to premises owned by the Trust but occupied exclusively by others unless agreed under specific Service Level Agreement (SLA) requiring the Trust to deliver to the occupier Ventilation Safety Management in accordance with this Policy.

This Policy is designed for the use of all staff involved with Ventilation activities, either as client or operator, and related equipment as defined in Health Technical Memorandum (HTM 03-01 Part A and Part B).

# Definitions

| Term | Definition |
| --- | --- |
| AE (V) | Authorising Engineer (Ventilation) |
| AP (V) | Authorised Person (Ventilation) |
| COSHH | Control of Substances Hazardous to Health regulations 2002 |
| CP (V) | Competent Person (Ventilation) |
| DP | Designated Person |
| HBN | Health Building Note |
| HSAWA | Health and Safety at Work etc. Act 1974 |
| HTM | Health Technical Memoranda |
| IPC | Infection Prevention and Control |
| MHSWR | Management of Health and Safety at Work Regulations 1999 |
| LEV | Local Exhaust Ventilation |
| Method Statement | A written instruction describing in a logical sequence how a task will be carried out in a way that secures health and safety and includes all control measures. |
| PPM | Planned Preventative Maintenance |
| Supplier / Contractor | An ELFT appointed company, contractor or partner who is responsible for undertaking maintenance activities (including PPM, reactive and remedial works) or project works on behalf of ELFT. |
| VSG | Ventilation Safety Group |

# Related Trust Policies & Procedures

The following Trust polices should be read in conjunction with this Policy.

- Health and Safety Policy

- Water Safety Policy

- Electrical Safety Policy

- Fire Safety Policy

- Estates Operational Policy (due for release in 2025)

# Roles and Responsibilities

Under Section 7 of the Health and Safety at Work Act etc., 1974 employees have a duty to take reasonable care for their own Health and Safety and of that of others who may be affected by their acts or omissions at work. Section 7 also requires the employee’s co-operation with their employer to enable the employer to comply with statutory duties for Health and Safety.

Employees should correctly use all work items provided by their employers, in accordance with their training and the instructions they receive to enable them to use / operate the items safely.

Employers or those they appoint (e.g. under Regulation 6) to assist them with Health and Safety matters therefore need to be informed, without delay, of any work situation which might present a serious and imminent danger. The danger could be to the employee concerned or a result of the employee's work to others.

Employees must also notify to their line manager any shortcomings in the Health and Safety arrangements, even when no immediate danger exists, so that employers in pursuit of their duties under the HSAWA and other statutory provisions can take such remedial action as may be required.

# Duties / Responsibilities

## Duty Holder – The Chief Executive Officer (CEO) and Board

The Chief Executive Officer (CEO) has the ultimate responsibility for the safety of patients, service users, staff and all other relevant persons within the Trust.  The CEO and Board have overall responsibility for ensuring the effective implementation of this Policy.  They have the ultimate managerial responsibility for the adequate allocation of resources, personnel and the organisation where Ventilation Systems are installed.

HTM 00 states that aspects of that responsibility can be assigned or delegated to a senior executive, but an independent audit system should be in place to assure them that the responsibilities are being discharged properly. The CEO has delegated the day-to-day management and control of Ventilation Systems, through the Director of Estates, Facilities & Capital Development to the Assistant Director of Estates, Engineering and Infrastructure and the Trust’s Authorised Persons (V).

## The Designated Person (DP) – Director of Estates, Facilities & Capital Development

The DP duties and responsibilities have been delegated to the Director of Estates, Facilities & Capital Development who provides the essential senior management link between the organisation and professional support, which also provides independence of the audit-reporting process.

The DP works closely with the Assistant Director of Estates, Engineering and Infrastructure (Senior Operational Manager (SOM)) to ensure that there is adequate provision to support Ventilation Safety.

The Designated Person’s responsibilities include.

- Leading on Health and Safety matters relating to Estates activities by informing the Board of any relevant Health and Safety management issues. This includes alerting them to the requirements of this Policy and any actual or potential breaches of Health and Safety Legislation.

- Formally appointing the roles within this Policy in writing.

- Ensuring that key Health and Safety information and instructions are cascaded and communicated throughout the Trust through a variety of routes, including the Trust’s Intranet.

- Monitoring the effectiveness of the of the Authorising Engineer (V) to ensure that they fulfil the requirements of their role.

## Senior Operational Manager (SOM) - Assistant Director of Estates - Engineering and Infrastructure

The SOM duties and responsibilities have been delegated to the Assistant Director of Estate – Engineering and Infrastructure.

The Senior Operational Manager has.

- Operational and professional responsibility for the Ventilation services.

- Access to robust, service-specific independent professional support which promotes and maintains the role of the informed client within the Trust.

## Authorising Engineer (Ventilation)

The Authorising Engineer (Ventilation) is a suitably qualified engineer who has been formally appointed in writing by the Trust’s Designated Person. They are independent of the operational structure of ELFT organisation.

### Duties and Responsibilities

The Authorising Engineer (Ventilation) duties and responsibilities include.

- Acting as an independent advisor to ELFT in accordance with HTM 00 (Policies and principles of healthcare engineering and HTM 03-01.

- Providing independent auditing and advice on the Trust’s Ventilation Systems.

- Acting as an assessor and making recommendations for the appointment of Authorised Persons (Ventilation)

- Monitoring the performance of the service.

- Conducting independent audits of Ventilation Systems, providing audit reports, and providing an annual audit report to the Designated Person (DP).

- Demonstrating understanding through familiarisation of the Ventilation Systems and attendance of an appropriate professional course(s).

- Assisting with the review of the Ventilation Policy and approving / identifying any changes to procedures.

- Assisting with the development of the estates risk register in relation to Ventilation Systems.

- Assisting in the development of a replacement Ventilation programme.

- Being a member of the Trust’s Ventilation Safety Group as defined in HTM 03-01.

### Training and Competence

| Requirement | Frequency |
| --- | --- |
| Formally appointed by the DP | Annual |
| Chartered or incorporated engineer with practical and relevant technical experience of the systems and equipment relevant to their appointment. | Not Applicable |
| Ability to demonstrate their competency and suitability for the role by demonstrating a good understanding of the management tasks involved and knowledge of HTM 03-01. | Annual |

## Authorised Persons (Ventilation)

The AP(V)s are individuals possessing sufficient technical knowledge and having received appropriate training to manage Ventilation Systems on a specific site or group of sites. They will have a good knowledge of the systems for which they are appointed and have a level of authority to make decisions about the system. They will be appointed in writing by the Designated Person following assessment by the AE (V). The AP(V) will assess and appoint Competent Persons (Ventilation) to work on the Ventilation Systems.

### Duties and Responsibilities

Their duties and responsibilities include.

- Effective responsibility for the on-site, day-to-day management and maintenance of the Ventilation Systems.

- Keeping the Trust’s Ventilation maintenance specification and schedule of equipment up to date.

- Being responsible for the practical implementation and operation of Management’s safety policy and procedures relating to the engineering aspects of Ventilation Systems

- Monitoring, in liaison with the Authorising Engineer (Ventilation), the implementation of this Policy and to feedback to the Ventilation Safety Group any significant issues such as non-compliance with this Policy.

- Maintaining copies of such documentation and other records required for the safe operation of the Ventilation Systems.

### Training and Competence

| Requirement | Frequency |
| --- | --- |
| Formally recommended by the AE (Ventilation) and appointed by the Trust’s DP | Annual |
| Satisfactorily completed an approved Competent Person (Ventilation) training course. | Not Applicable |
| Satisfactorily completed an approved Authorised Person (Ventilation) training course. | Not Applicable |
| Satisfactorily completed an approved Authorised Person (Ventilation) refresher training course. | Three years |

## Competent Person (Ventilation)

The Competent Person(s) (Ventilation) are individuals assessed by the Authorised Person as having sufficient technical knowledge and experience to carry out work on Ventilation Systems. They are formally appointed to this role.

### Duties and Responsibilities

Their duties and responsibilities include.

- Completing maintenance and periodic testing of the Trust’s Ventilation Systems in accordance with the relevant Approved Codes of Practice, installation and maintenance specifications.

- Carrying out repair, alteration or extension work, as directed by the Authorised Person (V)

- Reporting any Ventilation System maintenance that may disrupt ELFT’s operations to the AP(V).

- Performing engineering tests appropriate to all work carried out and present all test results to the Authorised Person (V) for final approval.

- Completing all work in accordance with The Trust’s Health & Safety Policy and all other relevant policies.

### Training and Competence

| Requirement | Frequency |
| --- | --- |
| Assessed and appointed by Management / Designated Person | Three years |
| Satisfactorily completed an approved Competent Person (Ventilation) training course. | Not Applicable |

## Infection Prevention and Control Doctor or Consultant Microbiologist

The Infection Prevention and Control Doctor or Consultant Microbiologist is the person nominated by ELFT’s management to advise on monitoring the infection control policy and microbiological performance of the system

## Infection, Prevention and Control (IPC) Team

The Trust’s Infection Prevention and Control (IPC) team is the source of in-house expertise and competence on a wide range of infection-related matter. The IPC team advises the Authorised Persons (Ventilation) and members of the Estates team on the potential vulnerability of specific patient groups and their susceptibility to airborne pathogens. The IPC team will also provide guidance on any special precautions that may be required when caring for these patients.

The advice of the IPC team will be sought at an early stage in the design of all projects, in the development of design quality standards related to hygiene materials and in any situation where works may impact infection control arrangements. The IPC team is responsible for working in conjunction with colleagues delivering maintenance and construction projects to ensure the estate remains safe and fit for purpose.

In addition, the IPC team will provide clinical advice and mentoring for maintenance staff on infection control principles and the prevention of healthcare associated infections (HCAIs). They will contribute to risk assessments related to the built environment, help identify priorities for the infection-control action plan, and support the monitoring and implementation of this policy.

## Capital Projects Team

The Capital Projects Team or the appointed Project Manager shall ensure that as-fitted drawings, operating manuals, maintenance instructions and commissioning manuals are made available and are stored in a safe place. They shall ensure that appointed contractors are sufficiently trained, competent and have the required competency to complete Ventilation System works.

## Contractor (Project Works)

The Contractor is the person or organisation responsible for the supply of the Ventilation equipment, its installation, commissioning, validation, verification or decommissioning. This person may be a representative of a specialist Ventilation organisation or a member of the general manager / chief executive’s staff.

# Maintenance of Ventilation Systems

All Ventilation Systems (air handling units (AHU), plant, ductwork and systems etc.) shall be included in the planned preventative maintenance (PPM) schedule .

Inspections and maintenance of heating and Ventilation Systems shall be carried out in accordance with  Health Technical Memorandum 03-01: Specialised Ventilation for healthcare premises Part A and B.

The general frequency of inspections and validation for Ventilation System shall consist of:

- All Ventilation Systems to be subject to inspection and maintenance annually.

- Ventilation Systems servicing critical care areas shall be inspected and maintained quarterly with actual performance measured and validated annually.

- Local Exhaust Ventilation (LEV) systems to be examined and tested every 14 months.

# Remedial Works

Any identified remedial works shall be completed within a reasonable period or escalated to the VSG.

# Records

It is imperative that all maintenance providers / contractors (including Private Finance Initiative (PFI), NHS Property Services (NHSPS), Community Health Partnership etc.) liaise with the Trust to ensure that they provide assurance to ELFT that the Ventilation in the buildings that they maintain is compliant with the relevant Ventilation safety legislation as outlined in this policy and the Health Technical Memorandum (HTM) 03-01 with all records (maintenance records, emergency works, validation reports etc.) provided to the Trust for inspection, auditing and storing.

These records shall be kept for a period of five years.

# Schematics

Up to date and accurate Ventilation drawings (schematics) shall be kept within the relevant switch room and provided to the Estates department. Ventilation drawings (schematics) shall be updated as part of any modification works or when there is a new Ventilation installation.

# Ventilation Spaces

Ventilation Spaces shall.

- Be regularly inspected.

- Be clean, tidy and not be used for storage with any items (cleaning products, old equipment etc.) removed from the area.

- Be secured / locked to prevent unauthorised access / operation.

# Incident Reporting

Any incident which involves the Ventilation Systems and which compromises safety, must be reported on InPhase and to the Estates Department. The reporting of injuries or dangerous occurrences, under the Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013 (RIDDOR), will be acted upon, as required, by the Health and Safety Department.

# Policy Review

This Policy will be reviewed within three years of the ratification date.

The Authorising Engineer (V) will monitor compliance during their regular audits. The Ventilation Safety Group will review any Authorising Engineer (V) audits recommendations and accordingly assess the compliance and effectiveness of the Ventilation Safety Policy.

The Ventilation Safety Policy will be reviewed by the Ventilation Safety Group in conjunction with the Health, Safety and Security team in the following circumstances.

- Following significant changes to relevant legislation and approved codes of practice

- When newly published material / evidence demonstrates a need for a change of existing working practices.

- Following a dangerous occurrence or “never event” or significant failure of any Ventilation System that may have placed patients, staff, volunteers or visitors at risk of harm or from Ventilation shock.

- When a review is identified as being required at the VSG meeting.

# Monitoring and Compliance

| Minimum requirement to be monitored monitoring against standards set out in Policy | Process for monitoring e.g. audit | Responsible individuals/ group/ committee | Frequency of monitoring/ audit/ reporting | Responsible individuals/ group/ committee for review of results and determining actions required |
| --- | --- | --- | --- | --- |
| Ventilation Safety Policy | Review | Ventilation Safety Group (VSG) | As per the Policy Review section of this Policy | Ventilation Safety Group |

# Monitoring Groups

## Ventilation Safety Group

The aim of the Ventilation Safety Group (VSG) is to provide leadership and direction to the Trust on all matters relating to Ventilation Safety and resilience required for the safe development and operation of the Trust’s premises. This is achieved through the assessment of information and reports from the operational team and the Authorising Engineer (Ventilation), and any other Trust groups, contractors, or stakeholders and by providing direction in sustaining operational Ventilation Safety plans and actions.

The VSG will be chaired by the Director of Estates, Facilities & Capital Development, it is a sub-committee of the Trust’s Health, Safety and Security Committee. The VSG reports to Health, Safety and Security Committee, which in turn reports to the Trust Board, and any other relevant parties (such as the Health and Safety Executive or CQC).

The VSGs aims are to.

- Ensure that suitable arrangements are in place to provide assurance that the Ventilation Assets / Systems used by the Trust are safe for use in the premises in which Trust staff work or operate.

- To support, review and provide feedback on the design, commissioning, validation, and Post Occupancy Evaluation process for new builds, refurbishments, and modifications to existing and new Assets / Systems

- To ensure new builds, refurbishments, modifications, and Assets / Systems are designed, installed, commissioned, and validated to the required standards.

- To support the review and prioritisation of the Asset Replacement programme

- To support decommissioning and removal of redundant Assets / Systems

- To consider the impact of Ventilation Assets / Systems and associated issues within Trust properties

- To review any CAS or Patient Safety Alerts relating to Ventilation Assets / Systems

- To review any Ventilation System related risks recorded in the ELFT reporting database.

- To ensure maintenance and monitoring procedures are in place and that records of all maintenance, inspection and testing activities are kept up to date and safely stored.

- To support the annual verification and performance testing programme

- Ensuring risks associated with Ventilation Systems are recognised and documented with action taken to minimise the risks through the operation of an action log system.

- Ensuring all tasks indicated by the risk assessments have been allocated and accepted.

- To determine the particular vulnerabilities of the at-risk population and to review risk assessments

- To agree and review remedial measures and actions, and ensure an action plan is in place, with agreed deadlines, to ensure any Health risks pertaining to Ventilation Systems are addressed.

- To ensure any Health risks pertaining to Ventilation Systems and Safety are addressed.

- To ensure the Ventilation Safety Policy is kept under review, including risk assessments and other associated documentation.

- To determine best use of available resources

- To be responsible for training and communication on Ventilation issues

## Infection Prevention and Control Committee

All major Ventilation Policy decisions should be made through the Infection, Prevention and Control Committee.  The Ventilation Safety Group will report to the Infection, Prevention and Control Committee.

## Health, Safety and Security Committee

All major Ventilation Policy decisions should be made through the Health, Safety & Security Committee.  The Ventilation Safety Group will report to the Health, Safety and Security Committee.  All Ventilation related issues that affect or impact on the Health, Safety and Wellbeing of any persons should be reported at the Health, Safety and Security Committee.

# References

- Health and Safety at Work etc Act 1974

- Control of Substances Hazardous to Health (COSHH) Regulations 2002

- Workplace (Health, Safety and Welfare) Regulations 1992

- Building Regulations Approved Documents L and F

- Health and Social Care Act 2008 (Regulated Activities) Regulations 2014

- The Medicines Act 1968 and Human Medicines Regulations 2012

- Building Act 1984

- Building Safety Act 2022

- Fire Safety Act 2021

- Construction (Design and Management) Regulations 2015

- Electricity at Work Regulations 1989

- Management of Health and Safety at Work Regulations 1999

- Provision and Use of Work Equipment Regulations 1998

- Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013 (RIDDOR)

- Workplace (Health, Safety and Welfare) Regulations 1992

- Regulatory Reform (Fire Safety) Order 2005

- CIBSE Guidance and associated Technical Memorandum (TM)

- BS EN 15780 Ventilation for buildings – Ductwork – Cleanliness of Ventilation Systems

- HSG 258 (Health and Safety Executive Guidance) Controlling airborne contaminants at work – A guide to local exhaust Ventilation (LEV)

- Health Technical Memorandum (HTM) 03-01 Specialised Ventilation for healthcare premises. Part – A: The concept, design, specification, installation and acceptance testing of healthcare Ventilation Systems.

- Health Technical Memorandum (HTM) 03-01 Specialised Ventilation for healthcare premises. Part – B: Operational Management and Performance Verification.

There are several other legal requirements that NHS Organisations, supporting professionals, contractors, and suppliers, must comply with. These are covered in the respective Health Building Notes (HBN’s), Health Technical Memoranda (HTM’s) and the NHS Premises Assurance Model (NHS PAM).

The Trust recognises its duties and legal responsibilities under these Act and Regulations and has compiled this Ventilation Safety Policy that sets out the planned approach for the Trust to achieve compliance with all relevant Health and Safety Legislation and Approved Codes of Practice (ACOP) within the Trust’s owned or maintained properties.

# Appendix A: Policy Equalities Impact Assessment

This checklist must be completed for all new policies to understand any potential impact on equalities and to assure equality in service delivery and employment.

| Policy Name: | Ventilation Safety Policy |
| --- | --- |
| Author: | Bevan Speariett |
| Role: | Assistant Director of Estates, Engineering and Infrastructure |
| Directorate: | Estates, Facilities & Capital Development |
| Date | 02/03/2025 |

- If any of the questions are answered ‘yes,’ then the proposed Policy is likely to be relevant to the Trust’s responsibilities under the equalities duties. Please provide the ratifying Committee with information on why ‘yes’ answers were given and whether or not this is justifiable for clinical reasons.

- The author should consult with the Associate Director of People & Culture to develop a more detailed assessment of the Policy’s impact and, where appropriate, design monitoring and reporting systems if there is any uncertainty.

- A copy of the completed form must be submitted to the relevant committee when submitting the document for ratification.

- The ratifying committee will inform you if they perceive the impact to be sufficient that a more detailed assessment is required.

| Equalities Impact Assessment Question | Yes | No | Always give further information if you answer “YES” |
| --- | --- | --- | --- |
| - How does the attached Policy/service fit into the Trusts overall aims? | Yes |  | The Policy has been created to meet the Trusts aims of providing and maintaining safe and health working conditions, equipment, and systems of work for all staff, patients and visitors, and to provide such resources, information, training and supervision as they need for this purpose. |
| - How will the Policy/service be implemented? | Yes |  | The Policy will be displayed on the Trust’s Intranet page and will be communicated via the Trust’s Ventilation Safety Group |
| - What outcomes are intended by implementing the Policy/delivering the service? | Yes |  | Effective control of Ventilation Systems |
| - How will the above outcomes be measured? | Yes |  | The outcomes will be measured via Audits, monitoring of compliance activities and via the ongoing Ventilation Safety Group meetings |
| - Who are they key stakeholders in respect of this Policy/service and how have they been involved? | Yes |  | The key stakeholders are the Ventilation Safety Group (VSG). |
| - Does this Policy/service impact on other policies or services? | Yes |  | Health and Safety Policy Estates Operational Policy (due for release in 2025) |
| - If YES is that impact understood? | Yes |  | No further comments |
| - Does this Policy/service impact on other agencies? |  | No | No further comments |
| - If YES is that impact understood? | Yes |  | No further comments |
| - Is there any data on the Policy or service that will help inform the equalities impact assessment? |  | No | No further comments |
| - Are there are information gaps, and how will they be addressed/what additional information is required? |  | No | No further comments |
| Equalities Impact Assessment Questions | Yes | No | Comment |
| - Does the Policy or service development have an adverse impact on any particular group? |  | No | No further comments |
| - Could the way the Policy is carried out have an adverse impact on equality of opportunity or good relations between different groups? |  | No | No further comments |
| - Where an adverse impact has been identified can changes be made to minimise it? |  | No | No further comments |
| - Is the Policy directly or indirectly discriminatory, and can the latter be justified? |  | No | No further comments |
| - Is the Policy intended to increase equality of opportunity by permitting Positive Action or Reasonable Adjustment? If so is this lawful? |  | No | The Policy is not intended to increase of equality of opportunity however elements of Positive Action or Reasonable Adjustment would be considered as part of Ventilation Safety. |

# Appendix B: Policy Submission Form / Checklist

To be completed and attached to any Policy or procedure submitted to the Trust Policy Group

| 1 | Details of Policy |  |
| --- | --- | --- |
| 1.1 | Title of Policy: | Ventilation Safety Policy |
| 1.3 | Author (job title) | Bevan Speariett (Assistant Director of Estates – Engineering and Infrastructure) |
| 1.4 | Lead / Sponsor Sub Committee | - David Stevens - Director of Estates, Facilities & Capital Development - Ventilation Safety Group |
| 1.5 | Reason for Policy | To ensure effective control of the Ventilation Systems |
| 1.6 | Who does Policy affect? | - Ventilation Safety Group - Infection Prevention and Control Committee - Health, Safety and Security Committee - Matrons / Lead Nurse - Ward or department managers - Clinical staff |
| 1.7 | Are national guidelines/codes of practice /best practice/ references incorporated and cited? | Yes |
| 1.8 | Has an Equality Impact Assessment been carried out? | Yes |
| 1.9 | Is this a revision of an existing Policy? | Yes |
| 1.10 | If yes have you identified the changes in the document? | Yes |
| 1.11 | Is the Policy in the correct format? | Yes |
| 2 | Information Collation |  |
| 2.1 | Where was Policy information obtained from? | Legislation, guidance and best practice as stated within this Policy |
| 3 | Policy Management |  |
| 3.1 | Is there a requirement for a new or revised management structure if the Policy is implemented? | No |
| 3.2 | If YES attach a copy to this form | Not Applicable |
| 3.3 | If NO explain why | No changes to management structure |
| 4 | Consultation Process |  |
| 4.1 | Was there internal/external consultation? | Yes |
| 4.2 | List groups / Persons involved | Ventilation Safety Group |
| 4.3 | Have internal/external comments been duly considered? | Yes |
| 4.4 | Date approved by relevant Sub-committee | Ventilation Safety Group (19th September 2024) |
| 4.5 | Signature of Subcommittee chair | David Stevens |
| 5 | Implementation |  |
| 5.1 | How and to whom will the Policy be distributed? | The Policy will be displayed on the Trust’s Intranet page and will be communicated via the Trust’s Ventilation Safety Group |
| 5.2 | If there are implementation requirements such as training, please detail? | ELFT training will be identified on the Estates training matrix. Hard FM Suppliers will conduct their own training to ensure competency |
| 5.3 | What is the cost of implementation and how will this be funded? | No significant costs apart from ongoing training which will be funded through the Estate budget |
| 6 | Monitoring |  |
| 6.1 | List the key performance indicators e.g. core standards | - Audits undertaken by Authorising Engineer (Ventilation) - Key Performance Indicators listed within Hard FM Supplier’s contractors |
| 6.2 | How will this be monitored and/or audited? | The outcomes will be measured via Audits, monitoring of compliance activities and via the Ventilation Safety Group meetings |
| 6.3 | Frequency of monitoring/audit | - Policy review every 3 (three) years |

Completed by Bevan Speariett

Date Policy approved by the Sponsor Committee: 3rd of March 2025

Date Policy approved by the Ratifying Committee: 21st of January 2026